## 153_155
S&C Power Fuses - Type SMD-50 (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-50 (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-50 (34.5 and 46 kV)
Standard Speed (TCC 153-1-5-5) | [9 empty] | Standard Speed (TCC 153-1-5-5) | [9 empty] | Standard Speed (TCC 153-1-5-5)
Total Clearing Time-Current Characteristic Curves Dated January 25, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 25, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 25, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
8602.47 | 0.018494 | 8602.47 | 0.018494 | 8602.47 | 0.018494 | 8602.47 | 0.018494 | 8602.47 | 0.018605 | 8602.47 | 0.018605 | 8602.47 | 0.018791 | 8602.47 | 0.018791 | 8602.47 | 0.019092 | 8602.47 | 0.019301 | 8602.47 | 0.020104 | 8602.47 | 0.021107 | 8602.47 | 0.022403
6277.88 | 0.022093 | 6411.12 | 0.021897 | 7706.34 | 0.019708 | 7869.89 | 0.019494 | 7972.87 | 0.019398 | 8289.98 | 0.019092 | 7178.14 | 0.020898 | 7330.48 | 0.020794 | 7783.79 | 0.020305 | 8240.38 | 0.019905 | 7737.23 | 0.021594 | 7221.34 | 0.024112 | 8281.69 | 0.023195
4782.77 | 0.025491 | 4913.67 | 0.025189 | 6277.88 | 0.022203 | 6443.26 | 0.021897 | 6547.19 | 0.02181 | 6855.41 | 0.021296 | 5749.02 | 0.023802 | 5900.46 | 0.02359 | 6353.68 | 0.022989 | 6807.58 | 0.022492 | 6303.05 | 0.024989 | 5795.19 | 0.028689 | 6848.55 | 0.027299
3287.08 | 0.030603 | 3417.82 | 0.030091 | 4845.35 | 0.025491 | 5012.94 | 0.025089 | 5114.21 | 0.02489 | 5425.04 | 0.024304 | 4318.96 | 0.028014 | 4468.34 | 0.027709 | 4923.51 | 0.026896 | 5376.43 | 0.02621 | 4874.51 | 0.03021 | 4362.37 | 0.036704 | 5419.62 | 0.0339
1793.14 | 0.039582 | 1925.09 | 0.038688 | 3417.82 | 0.0303 | 3582.3 | 0.029704 | 3687.71 | 0.029499 | 3998.86 | 0.028689 | 2889.24 | 0.034891 | 3037.38 | 0.034409 | 3493.85 | 0.0332 | 3947.21 | 0.032097 | 3445.27 | 0.039898 | 4306.02 | 0.037218 | 5338.93 | 0.034511
299.058 | 0.074304 | 429.944 | 0.069865 | 1987.69 | 0.038496 | 2151.1 | 0.037702 | 2256.88 | 0.037218 | 2567.64 | 0.036018 | 1457.84 | 0.052379 | 1607.96 | 0.050891 | 2064.68 | 0.047191 | 2516.8 | 0.044284 | 3397.37 | 0.040416 | 4178.75 | 0.038192 | 5201.9 | 0.035309
294.311 | 0.074896 | 420.168 | 0.070703 | 558.173 | 0.066414 | 721.752 | 0.062821 | 826.078 | 0.060795 | 1137.63 | 0.056095 | 1424.69 | 0.053112 | 1579.27 | 0.051604 | 2033.94 | 0.047709 | 2486.77 | 0.044815 | 3277.24 | 0.041598 | 3896.23 | 0.04082 | 5028 | 0.036486
284.472 | 0.076021 | 403.289 | 0.072122 | 544.936 | 0.067077 | 711.718 | 0.063322 | 813.778 | 0.06128 | 1110.65 | 0.05688 | 1344.41 | 0.05532 | 1535.66 | 0.052587 | 1977.78 | 0.048715 | 2427.8 | 0.045578 | 3161.35 | 0.042984 | 3582.3 | 0.044196 | 4787.55 | 0.038382
274.962 | 0.077085 | 381.324 | 0.074082 | 526.718 | 0.068423 | 685.179 | 0.064528 | 787.361 | 0.062509 | 1075.67 | 0.058079 | 1266.11 | 0.057791 | 1476.92 | 0.054017 | 1896.43 | 0.050188 | 2351.34 | 0.046817 | 3037.38 | 0.044416 | 3326.77 | 0.047615 | 4554.05 | 0.040296
263.126 | 0.07871 | 360.196 | 0.076323 | 508.601 | 0.069727 | 664.927 | 0.065692 | 755.73 | 0.064081 | 1041.79 | 0.059303 | 1158.29 | 0.061585 | 1404.89 | 0.055983 | 1812.98 | 0.052119 | 2265.92 | 0.048185 | 2924.12 | 0.046079 | 3064.84 | 0.051809 | 4166.23 | 0.044284
247.554 | 0.081091 | 336.179 | 0.079181 | 491.107 | 0.070985 | 641.415 | 0.067011 | 719.59 | 0.066085 | 997.945 | 0.060976 | 1077.82 | 0.065172 | 1316.47 | 0.058776 | 1714.24 | 0.054394 | 2181.43 | 0.049791 | 2710.11 | 0.049299 | 2795.45 | 0.05722 | 3888.44 | 0.047709
235.244 | 0.083213 | 299.058 | 0.084967 | 452.442 | 0.074304 | 612.576 | 0.068901 | 674.302 | 0.068832 | 944.538 | 0.063322 | 987.027 | 0.069796 | 1232.38 | 0.061891 | 1598.34 | 0.057677 | 2081.27 | 0.051809 | 2524.36 | 0.052902 | 2601.24 | 0.06183 | 3585.88 | 0.052223
219.34 | 0.086328 | 268.441 | 0.091176 | 418.072 | 0.07801 | 580.373 | 0.071197 | 616.263 | 0.073132 | 894.883 | 0.065823 | 912.049 | 0.074674 | 1145.62 | 0.065692 | 1427.55 | 0.063511 | 1958.1 | 0.05461 | 2337.27 | 0.056993 | 2442.41 | 0.066612 | 3336.76 | 0.056711
205.125 | 0.08956 | 237.371 | 0.099702 | 385.928 | 0.081982 | 549.313 | 0.073789 | 572.877 | 0.077009 | 841.924 | 0.068696 | 845.299 | 0.079892 | 1058.59 | 0.070074 | 1303.37 | 0.068969 | 1853.31 | 0.05722 | 2106.39 | 0.063385 | 2290.99 | 0.071907 | 3016.2 | 0.064081
190.302 | 0.093654 | 212.219 | 0.10892 | 351.302 | 0.087537 | 507.078 | 0.077778 | 535.75 | 0.08093 | 784.217 | 0.072625 | 779.526 | 0.086328 | 988.015 | 0.074599 | 1198.35 | 0.074822 | 1733.2 | 0.060916 | 1927.02 | 0.069865 | 2136.09 | 0.078165 | 2759.34 | 0.071693
176.375 | 0.098521 | 187.282 | 0.12162 | 317.869 | 0.094214 | 471.378 | 0.081982 | 492.583 | 0.086414 | 728.278 | 0.077009 | 708.168 | 0.094966 | 904.781 | 0.081011 | 1110.65 | 0.08077 | 1645.37 | 0.064017 | 1729.73 | 0.079024 | 1963.98 | 0.087017 | 2469.43 | 0.082636
160.711 | 0.1052 | 170.138 | 0.13352 | 289.06 | 0.1018 | 439.948 | 0.086328 | 447.044 | 0.093654 | 674.302 | 0.082064 | 655.683 | 0.10282 | 830.219 | 0.088235 | 1019.12 | 0.088499 | 1532.59 | 0.068491 | 1558.87 | 0.089738 | 1794.94 | 0.097838 | 2272.73 | 0.092728
147.467 | 0.11221 | 151.806 | 0.15072 | 263.916 | 0.11022 | 398.478 | 0.09319 | 398.877 | 0.10395 | 634.397 | 0.086758 | 605.875 | 0.11221 | 753.466 | 0.097547 | 932.337 | 0.097741 | 1460.76 | 0.071979 | 1427.55 | 0.1002 | 1670.24 | 0.10795 | 2046.18 | 0.1072
130.398 | 0.12492 | 139.296 | 0.16629 | 240.718 | 0.12005 | 365.639 | 0.1005 | 353.77 | 0.11665 | 595.661 | 0.091812 | 540.593 | 0.12832 | 686.55 | 0.10827 | 856.36 | 0.10795 | 1390.91 | 0.07587 | 1308.59 | 0.11277 | 1565.12 | 0.11816 | 1879.44 | 0.12125
115.884 | 0.13962 | 123.42 | 0.1934 | 219.779 | 0.13167 | 330.512 | 0.11033 | 315.337 | 0.13233 | 551.515 | 0.098619 | 494.063 | 0.14385 | 641.415 | 0.11711 | 778.747 | 0.12125 | 1321.75 | 0.08013 | 1195.96 | 0.12755 | 1424.69 | 0.13525 | 1719.39 | 0.13865
103.294 | 0.15745 | 108.591 | 0.2292 | 201.465 | 0.14456 | 296.082 | 0.1232 | 283.053 | 0.14982 | 497.036 | 0.10979 | 453.801 | 0.16029 | 599.846 | 0.12705 | 712.43 | 0.13579 | 1239.8 | 0.085986 | 1093.02 | 0.14542 | 1315.15 | 0.15238 | 1577.69 | 0.1584
92.627 | 0.17809 | 97.8645 | 0.26577 | 185.975 | 0.15855 | 268.173 | 0.13715 | 251.295 | 0.17338 | 460.199 | 0.11934 | 421.009 | 0.17774 | 547.667 | 0.14256 | 642.056 | 0.15652 | 1180.51 | 0.090904 | 952.125 | 0.17809 | 1211.61 | 0.17184 | 1424.69 | 0.18642
83.6445 | 0.20184 | 88.1093 | 0.31155 | 171.848 | 0.17407 | 245.581 | 0.15192 | 230.356 | 0.19475 | 416.82 | 0.13405 | 390.587 | 0.19767 | 512.687 | 0.15543 | 583.282 | 0.17951 | 1117.33 | 0.096968 | 867.566 | 0.2063 | 1097.4 | 0.20044 | 1300.77 | 0.2168
72.2093 | 0.24571 | 78.9309 | 0.37033 | 156.743 | 0.19611 | 226.02 | 0.16762 | 211.372 | 0.22006 | 384.387 | 0.14775 | 354.478 | 0.22739 | 473.268 | 0.17355 | 533.611 | 0.20467 | 1049.11 | 0.10509 | 791.307 | 0.23921 | 977.206 | 0.24232 | 1198.35 | 0.24965
61.9645 | 0.30755 | 70.0751 | 0.44993 | 145.707 | 0.21659 | 206.979 | 0.18791 | 195.511 | 0.2462 | 352.71 | 0.16465 | 333.5 | 0.24989 | 436.879 | 0.19475 | 485.249 | 0.23637 | 990.983 | 0.11277 | 729.006 | 0.27381 | 885.978 | 0.28547 | 1128.56 | 0.27682
55.2327 | 0.3674 | 62.9639 | 0.53856 | 134.639 | 0.24208 | 188.597 | 0.21381 | 173.228 | 0.29528 | 323.967 | 0.18458 | 310.642 | 0.27875 | 404.5 | 0.21788 | 442.154 | 0.27354 | 902.071 | 0.12743 | 680.399 | 0.30725 | 795.274 | 0.34238 | 1064.96 | 0.30786
50.2269 | 0.42813 | 55.5096 | 0.6721 | 123.915 | 0.27218 | 168.108 | 0.25214 | 153.332 | 0.36018 | 297.269 | 0.20815 | 286.184 | 0.31654 | 374.521 | 0.24498 | 389.807 | 0.33698 | 840.242 | 0.14004 | 641.415 | 0.34035 | 727.55 | 0.39819 | 1004.95 | 0.34272
46.2724 | 0.48957 | 50.1265 | 0.80689 | 115.537 | 0.3027 | 150.145 | 0.29912 | 140.274 | 0.41639 | 273.591 | 0.2345 | 261.813 | 0.36631 | 350.951 | 0.27164 | 362.726 | 0.38192 | 788.148 | 0.15313 | 596.854 | 0.38573 | 685.864 | 0.44284 | 952.125 | 0.3804
43.2736 | 0.54991 | 45.2203 | 0.96871 | 106.76 | 0.34136 | 138.739 | 0.33765 | 127.179 | 0.49397 | 245.827 | 0.27544 | 241.441 | 0.41971 | 323.643 | 0.30908 | 337.189 | 0.43198 | 725.37 | 0.17286 | 561.532 | 0.42728 | 649.808 | 0.48377 | 880.678 | 0.44065
40.835 | 0.60674 | 41.9946 | 1.1155 | 98.7493 | 0.38688 | 130.138 | 0.37366 | 119.892 | 0.54394 | 217.81 | 0.332 | 212.432 | 0.52016 | 302.971 | 0.34512 | 320.423 | 0.47379 | 666.925 | 0.19591 | 530.949 | 0.4705 | 616.263 | 0.53324 | 831.881 | 0.49152
38.5339 | 0.67011 | 39.4699 | 1.2529 | 90.6114 | 0.44549 | 123.173 | 0.40698 | 112.91 | 0.59896 | 197.871 | 0.38919 | 192.215 | 0.62076 | 274.138 | 0.4082 | 305.405 | 0.51604 | 577.478 | 0.24474 | 509.11 | 0.50891 | 587.38 | 0.58426 | 784.217 | 0.5543
35.8568 | 0.76248 | 37.3202 | 1.4018 | 83.4774 | 0.51043 | 116.932 | 0.44416 | 106.653 | 0.66282 | 175.671 | 0.47614 | 175.495 | 0.72842 | 253.567 | 0.46771 | 294.017 | 0.55485 | 504.044 | 0.30573 | 489.636 | 0.54882 | 551.515 | 0.65823 | 740.024 | 0.62261
33.466 | 0.86242 | 35.9645 | 1.5102 | 78.5372 | 0.56824 | 111.006 | 0.48618 | 98.3551 | 0.76551 | 157.056 | 0.58022 | 161.516 | 0.84462 | 231.048 | 0.54991 | 278.004 | 0.61402 | 456.989 | 0.36053 | 470.436 | 0.58951 | 520.956 | 0.73642 | 701.823 | 0.69381
31.6433 | 0.95628 | 34.4852 | 1.6449 | 74.7815 | 0.62261 | 104.646 | 0.53589 | 92.7197 | 0.8556 | 143.251 | 0.68152 | 150.747 | 0.95818 | 211.372 | 0.64209 | 267.102 | 0.66282 | 409.384 | 0.43672 | 440.388 | 0.66878 | 490.126 | 0.83295 | 669.598 | 0.76551
29.6518 | 1.0773 | 33.2325 | 1.7774 | 69.7256 | 0.70423 | 99.5425 | 0.58484 | 85.9338 | 0.98423 | 129.101 | 0.82636 | 140.836 | 1.0968 | 188.597 | 0.79102 | 257.657 | 0.71126 | 381.706 | 0.49545 | 417.655 | 0.74525 | 461.121 | 0.94401 | 626.203 | 0.88323
27.2355 | 1.2592 | 31.9614 | 1.9398 | 65.7963 | 0.78398 | 93.7453 | 0.65043 | 81.9882 | 1.0806 | 120.132 | 0.94495 | 131.314 | 1.2529 | 173.401 | 0.93283 | 246.812 | 0.77315 | 361.278 | 0.54502 | 389.417 | 0.86071 | 439.069 | 1.0457 | 597.451 | 0.97936
25.3941 | 1.4385 | 30.862 | 2.0939 | 62.3998 | 0.86157 | 86.2783 | 0.75494 | 77.5228 | 1.2053 | 112.797 | 1.0677 | 123.05 | 1.4271 | 163.794 | 1.0436 | 234.54 | 0.85475 | 343.657 | 0.59658 | 367.472 | 0.97064 | 423.967 | 1.1311 | 561.532 | 1.1288
23.8913 | 1.6141 | 29.7112 | 2.2762 | 58.7657 | 0.96967 | 79.8839 | 0.86844 | 73.3006 | 1.3485 | 106.228 | 1.1958 | 116.815 | 1.5918 | 153.792 | 1.1875 | 221.323 | 0.96487 | 330.182 | 0.644 | 347.459 | 1.0913 | 407.75 | 1.2393 | 530.419 | 1.287
22.6806 | 1.7827 | 28.7754 | 2.4571 | 56.1236 | 1.0646 | 74.5575 | 0.99012 | 70.2154 | 1.4775 | 101.553 | 1.3128 | 109.902 | 1.8239 | 145.271 | 1.3392 | 208.225 | 1.0979 | 314.078 | 0.70914 | 327.223 | 1.2418 | 394.908 | 1.3272 | 504.044 | 1.4528
21.6176 | 1.963 | 27.6747 | 2.6842 | 53.7613 | 1.163 | 69.8652 | 1.1221 | 66.724 | 1.6498 | 96.5039 | 1.4586 | 104.646 | 2.0264 | 136.947 | 1.5268 | 198.466 | 1.2162 | 297.864 | 0.78398 | 310.021 | 1.4018 | 382.088 | 1.4299 | 485.734 | 1.5855
20.7699 | 2.1338 | 26.5364 | 2.9734 | 51.6532 | 1.2604 | 65.5337 | 1.273 | 63.3429 | 1.8531 | 92.9054 | 1.5777 | 98.947 | 2.308 | 130.66 | 1.6946 | 190.302 | 1.3312 | 283.904 | 0.86071 | 296.378 | 1.5497 | 367.105 | 1.5761 | 472.322 | 1.7048
19.8758 | 2.345 | 25.5214 | 3.2579 | 49.6774 | 1.3674 | 62.1506 | 1.4172 | 60.4345 | 2.0609 | 89.0839 | 1.7321 | 93.2777 | 2.6471 | 124.411 | 1.8978 | 183.023 | 1.4629 | 268.71 | 0.96105 | 282.205 | 1.7528 | 354.478 | 1.7218 | 456.076 | 1.8753
19.1347 | 2.5516 | 24.6189 | 3.5697 | 47.5864 | 1.4982 | 58.8245 | 1.5887 | 57.7173 | 2.3035 | 85.5052 | 1.8959 | 89.7995 | 2.9062 | 118.699 | 2.1338 | 176.198 | 1.5966 | 256.629 | 1.0551 | 270.598 | 1.9417 | 341.943 | 1.8828 | 439.509 | 2.0671
18.366 | 2.8069 | 23.8435 | 3.8919 | 45.0848 | 1.6679 | 55.7878 | 1.7756 | 55.1775 | 2.5796 | 81.2536 | 2.1317 | 85.0787 | 3.3266 | 113.023 | 2.4184 | 170.82 | 1.7269 | 244.601 | 1.1641 | 263.126 | 2.0919 | 330.512 | 2.0548 | 421.009 | 2.3241
17.7342 | 3.0572 | 23.162 | 4.2013 | 43.2736 | 1.8348 | 53.12 | 1.9708 | 52.7494 | 2.8947 | 77.4453 | 2.3944 | 80.6867 | 3.842 | 108.049 | 2.7083 | 165.109 | 1.8772 | 232.671 | 1.296 | 254.584 | 2.2852 | 318.187 | 2.2784 | 406.935 | 2.5567
17.1585 | 3.3101 | 22.0764 | 4.809 | 41.2042 | 2.0365 | 50.4282 | 2.205 | 50.8333 | 3.2161 | 73.8156 | 2.6816 | 76.2923 | 4.4949 | 103.605 | 3.0451 | 160.39 | 2.0124 | 223.547 | 1.4256 | 246.812 | 2.5089 | 304.795 | 2.5618 | 393.725 | 2.8181
16.5352 | 3.6341 | 21.3811 | 5.2954 | 39.3123 | 2.2626 | 47.9207 | 2.4767 | 48.645 | 3.6558 | 70.992 | 2.9645 | 73.5945 | 5.0188 | 99.7418 | 3.4001 | 155.183 | 2.205 | 212.644 | 1.5966 | 239.757 | 2.7272 | 295.786 | 2.8181 | 379.802 | 3.1248
15.9027 | 4.0216 | 20.7699 | 5.7964 | 37.7708 | 2.4767 | 45.3108 | 2.8237 | 46.9718 | 4.0942 | 68.2765 | 3.2872 | 70.992 | 5.615 | 96.1186 | 3.8002 | 150.295 | 2.4016 | 204.51 | 1.7528 | 231.51 | 3.012 | 284.188 | 3.1749 | 368.576 | 3.4341
15.3251 | 4.4504 | 20.2368 | 6.2883 | 35.8927 | 2.7875 | 43.534 | 3.1372 | 45.3561 | 4.5987 | 65.1416 | 3.744 | 68.4817 | 6.3385 | 93.1845 | 4.2348 | 144.691 | 2.663 | 196.687 | 1.9282 | 224.443 | 3.3101 | 277.448 | 3.4752 | 359.476 | 3.7515
14.9019 | 4.8185 | 19.6977 | 6.8969 | 34.6235 | 3.03 | 41.7852 | 3.4683 | 43.7523 | 5.1964 | 62.901 | 4.1186 | 66.3248 | 7.1409 | 90.5208 | 4.7238 | 139.574 | 2.9704 | 189.732 | 2.1191 | 216.29 | 3.6777 | 268.441 | 3.8958 | 349.899 | 4.1391
14.447 | 5.3112 | 19.2691 | 7.4673 | 33.4995 | 3.2807 | 40.1065 | 3.8573 | 42.1208 | 5.9245 | 60.9199 | 4.5352 | 64.4934 | 7.9971 | 88.1093 | 5.2954 | 134.236 | 3.3465 | 181.565 | 2.3849 | 209.478 | 4.086 | 263.916 | 4.2474 | 343.314 | 4.4726
14.034 | 5.8484 | 18.8121 | 8.2064 | 32.5419 | 3.5204 | 38.4953 | 4.2984 | 40.7534 | 6.7144 | 58.7657 | 5.079 | 62.8381 | 8.956 | 85.4197 | 6.0433 | 128.714 | 3.8154 | 173.401 | 2.7083 | 204.92 | 4.4372 | 257.657 | 4.7004 | 336.179 | 4.8909
13.6465 | 6.5108 | 18.3843 | 9.0006 | 31.454 | 3.8267 | 37.0228 | 4.7947 | 39.5094 | 7.5794 | 57.2002 | 5.5706 | 60.9199 | 10.282 | 83.3106 | 6.8559 | 125.16 | 4.2348 | 166.103 | 3.0512 | 199.86 | 4.8618 | 252.808 | 5.1707 | 329.192 | 5.3696
13.4031 | 7.0213 | 18.0744 | 9.8033 | 30.3721 | 4.2096 | 35.8927 | 5.2275 | 38.4953 | 8.5051 | 55.6207 | 6.1646 | 59.5347 | 11.7226 | 80.7675 | 8.1819 | 122.314 | 4.6262 | 160.069 | 3.4272 | 195.511 | 5.3059 | 248.298 | 5.7562 | 322.029 | 5.9539
13.0721 | 7.7778 | 17.752 | 10.6988 | 29.3861 | 4.6079 | 35.0415 | 5.5872 | 37.5073 | 9.5723 | 54.139 | 6.7747 | 58.6483 | 13.2066 | 78.6158 | 9.7064 | 119.652 | 5.1553 | 154.718 | 3.8192 | 191.065 | 5.901 | 243.137 | 6.4978 | 316.6 | 6.5108
12.7239 | 8.6672 | 17.4877 | 11.6298 | 28.4322 | 5.0841 | 34.1763 | 6.0254 | 36.6544 | 10.6458 | 52.8022 | 7.4599 | 57.5444 | 15.2982 | 76.5215 | 11.7459 | 117.166 | 5.7849 | 150.446 | 4.168 | 187.282 | 6.485 | 237.134 | 7.4525 | 310.952 | 7.1693
12.447 | 9.6679 | 17.2791 | 12.7807 | 27.2627 | 5.7163 | 33.3991 | 6.5108 | 36.0366 | 11.8279 | 51.6016 | 8.2308 | 56.5178 | 18.1306 | 74.6321 | 14.2281 | 114.273 | 6.5888 | 147.467 | 4.4949 | 183.39 | 7.2337 | 232.671 | 8.421 | 304.795 | 7.9259
12.1883 | 10.881 | 17.0559 | 14.1999 | 26.5364 | 6.2076 | 32.7378 | 6.9865 | 35.5 | 13.0761 | 50.681 | 9.0274 | 55.6207 | 22.1153 | 72.935 | 17.7739 | 112.571 | 7.3569 | 144.691 | 4.8329 | 179.938 | 8.029 | 228.292 | 9.5533 | 297.864 | 9.1176
11.9589 | 12.6167 | 16.8693 | 15.7141 | 25.8037 | 6.7679 | 31.9614 | 7.5945 | 35.0064 | 15.0271 | 49.8267 | 9.9505 | 54.9572 | 26.5768 | 71.993 | 20.0241 | 110.012 | 8.5815 | 142.252 | 5.2379 | 176.375 | 9.0006 | 223.995 | 11.0553 | 292.258 | 10.2209
11.8281 | 13.9206 | 16.6847 | 17.5808 | 25.1665 | 7.3132 | 31.3912 | 8.1738 | 34.4852 | 17.9335 | 49.1831 | 10.8594 | 54.5738 | 32.2252 | 71.3479 | 22.5815 | 107.941 | 9.8913 | 139.854 | 5.688 | 173.922 | 10.0099 | 219.779 | 12.7934 | 286.757 | 11.6182
11.687 | 15.6052 | 16.5352 | 19.7671 | 24.6929 | 7.8788 | 30.7696 | 8.8235 | 34.1421 | 20.4258 | 48.2574 | 12.3686 | 54.5738 | 39.779 | 70.4263 | 26.5504 | 105.803 | 11.4578 | 137.496 | 6.2447 | 170.649 | 11.2324 | 215.427 | 15.2073 | 281.36 | 13.4182
11.5939 | 17.4937 | 16.3871 | 22.2696 | 24.2281 | 8.4546 | 30.1904 | 9.7064 | 33.8024 | 24.3523 | 47.3018 | 14.3416 | 54.5738 | 49.0548 | 69.7953 | 30.4816 | 103.916 | 13.4449 | 135.043 | 6.9657 | 167.94 | 12.5917 | 210.739 | 18.2027 | 276.617 | 15.3439
11.513 | 19.7868 | 16.2565 | 25.264 | 23.8435 | 9.1721 | 29.7409 | 10.4053 | 33.6001 | 28.604 | 46.5975 | 16.58 | 54.5738 | 65.1077 | 69.17 | 35.3792 | 101.96 | 16.3024 | 132.502 | 7.7855 | 165.771 | 14.0456 | 206.359 | 22.8296 | 272.226 | 17.4243
11.4556 | 22.1153 | 16.1431 | 28.6609 | 23.465 | 9.9901 | 29.2688 | 11.4464 | 33.533 | 33.7319 | 45.8578 | 19.7083 | 54.5738 | 85.5596 | 68.4817 | 43.4992 | 99.443 | 21.2538 | 130.529 | 8.65 | 163.466 | 15.5124 | 202.678 | 28.5473 | 267.905 | 20.0639
11.3756 | 25.5415 | 16.0465 | 32.0656 | 23.0695 | 10.946 | 28.9776 | 12.3073 | 33.466 | 39.2297 | 45.4469 | 23.3572 | 54.5738 | 123.563 | 67.8681 | 54.2856 | 98.0604 | 25.5415 | 128.457 | 9.7064 | 161.355 | 17.4937 | 199.062 | 34.9253 | 262.337 | 24.2316
11.3529 | 29.9711 | 15.9346 | 37.2177 | 22.7943 | 11.8396 | 28.7179 | 13.3252 | 33.2991 | 47.1438 | 44.9947 | 27.4625 | 54.5738 | 169.969 | 67.3273 | 67.7467 | 96.9876 | 30.0606 | 126.544 | 10.881 | 159.43 | 19.7279 | 195.706 | 45.9418 | 258.69 | 27.7642
11.3416 | 34.6144 | 15.8868 | 42.9411 | 22.5224 | 12.9726 | 28.347 | 15.2224 | 33.1661 | 57.0499 | 44.5916 | 32.8719 | 54.5738 | 228.069 | 66.8576 | 88.4108 | 95.7349 | 36.8133 | 124.91 | 12.1012 | 157.528 | 22.4027 | 192.6 | 59.2446 | 255.093 | 32.1293
11.3416 | 40.6983 | 15.8551 | 49.3971 | 22.276 | 14.0875 | 28.2904 | 17.4589 | 33.0668 | 69.1061 | 44.3691 | 38.9966 | 54.5738 | 306.029 | 66.3248 | 117.226 | 94.972 | 43.0692 | 123.173 | 13.9899 | 155.805 | 26.0023 | 189.732 | 75.644 | 251.547 | 37.107
11.3416 | 49.5445 | 15.8551 | 57.5622 | 22.1206 | 15.4663 | 28.2904 | 20.2441 | 32.9677 | 84.6298 | 44.1478 | 49.348 | 54.5193 | 429.411 | 66.1262 | 161.252 | 93.8391 | 52.7965 | 121.339 | 16.0453 | 154.1 | 29.236 | 187.282 | 94.9657 | 248.049 | 42.8984
11.3416 | 59.836 | 15.8393 | 69.0375 | 21.9883 | 17.0138 | 28.2904 | 24.1355 | 32.9019 | 98.1303 | 44.0596 | 60.1937 | 54.5193 | 520.674 | 65.8622 | 210.437 | 92.9983 | 67.2105 | 119.892 | 18.772 | 152.262 | 34.3746 | 184.678 | 124.301 | 245.09 | 48.4735
11.3416 | 74.6735 | 15.8393 | 82.0635 | 21.8786 | 18.6976 | 28.2904 | 28.775 | 32.9019 | 120.054 | 44.0596 | 76.7033 | 54.5193 | 577.34 | 65.8622 | 270.563 | 91.9809 | 85.9857 | 118.343 | 21.9839 | 150.446 | 40.8198 | 182.657 | 159.341 | 242.167 | 56.3179
11.3416 | 93.7472 | 15.8393 | 100.398 | 21.8786 | 21.0019 | 28.2904 | 35.0295 | 32.9019 | 146.877 | 44.0156 | 103.846 | 54.5193 | 600.146 | 65.8622 | 332.66 | 91.3392 | 104.987 | 117.166 | 25.3897 | 148.502 | 53.5359 | 181.202 | 207.119 | 239.039 | 64.5282
11.3416 | 118.632 | 15.8393 | 118.044 | 21.8786 | 23.6607 | 28.2904 | 45.4426 | 32.9019 | 184.393 | 43.9716 | 130.761 | 54.5193 | 600.146 | 65.8622 | 414.738 | 90.7928 | 126.67 | 116.116 | 29.6454 | 147.319 | 64.1447 | 179.938 | 258.735 | 235.951 | 76.7033
11.3416 | 149.082 | 15.8393 | 137.967 | 21.8786 | 27.7918 | 28.2904 | 58.8925 | 32.9019 | 229.432 | 43.796 | 176.508 | 54.5193 | 600.146 | 65.8622 | 491.035 | 90.34 | 155.124 | 114.846 | 35.8747 | 146.145 | 76.4751 | 178.683 | 326.117 | 233.37 | 88.851
11.3302 | 202.24 | 15.8393 | 162.862 | 21.8786 | 32.3857 | 28.2904 | 74.6735 | 32.9019 | 271.64 | 43.7523 | 238.732 | 54.5193 | 600.146 | 65.8622 | 565.983 | 89.7995 | 201.638 | 113.93 | 42.8133 | 144.836 | 98.1303 | 177.436 | 415.15 | 230.817 | 101.602
11.3302 | 258.992 | 15.8393 | 201.838 | 21.8786 | 38.5728 | 28.2904 | 86.844 | 32.9019 | 367.037 | 43.6649 | 305.422 | 54.5193 | 600.146 | 65.8622 | 600.146 | 89.3516 | 255.669 | 113.023 | 51.964 | 143.969 | 115.492 | 176.375 | 498.902 | 228.063 | 122.22
11.3302 | 319.702 | 15.8393 | 248.162 | 21.8786 | 45.7597 | 28.2904 | 108.163 | 32.9019 | 453.524 | 43.6212 | 375.52 | 54.5193 | 600.146 | 65.8622 | 600.146 | 88.7283 | 336.315 | 112.459 | 61.2188 | 142.822 | 141.015 | 175.846 | 559.277 | 225.794 | 146.877
11.3302 | 399.771 | 15.8393 | 305.725 | 21.8786 | 56.7109 | 28.2904 | 129.726 | 32.9019 | 529.541 | 43.4471 | 473.786 | 54.5193 | 600.146 | 65.8622 | 600.146 | 88.2857 | 422.64 | 111.563 | 74.9708 | 142.252 | 170.815 | 175.144 | 600.146 | 223.547 | 178.27
11.3302 | 488.602 | 15.8393 | 366.673 | 21.8786 | 68.3551 | 28.2904 | 164.488 | 32.9019 | 573.34 | 43.3602 | 550.458 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.8454 | 513.993 | 111.228 | 87.1032 | 141.826 | 216.372 | 175.144 | 600.146 | 221.323 | 209.187
11.3302 | 571.066 | 15.8393 | 436.29 | 21.8786 | 80.1302 | 28.2904 | 205.684 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.6699 | 578.488 | 110.674 | 106.035 | 138.0384 | 278.747 | 175.144 | 600.146 | 219.999 | 251.638
11.3302 | 600.146 | 15.8393 | 503.882 | 21.8786 | 94.3076 | 28.2904 | 248.409 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 110.232 | 127.554 | 141.26 | 359.46 | 175.144 | 600.146 | 218.683 | 299.117
11.3302 | 600.146 | 15.8234 | 573.34 | 21.8786 | 113.897 | 28.2904 | 301.803 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 109.902 | 173.897 | 141.26 | 461.247 | 175.144 | 600.146 | 217.592 | 361.968
11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 134.984 | 28.2904 | 377.765 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 109.572 | 223.583 | 141.26 | 569.367 | 175.144 | 600.146 | 216.29 | 446.816
11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 156.052 | 28.2904 | 467.242 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 109.353 | 282.651 | 141.118 | 600.146 | 175.144 | 600.146 | 215.427 | 553.749
11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 186.419 | 28.2904 | 552.65 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 108.917 | 347.868 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146
11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 222.917 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 108.482 | 424.744 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146
11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 282.37 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 108.157 | 488.117 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146
11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 346.833 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 107.833 | 568.802 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146
11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 423.901 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 107.725 | 600.146 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146
11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 500.391 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 107.725 | 600.146 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146
11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 564.86 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 107.725 | 600.146 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146
11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 600.146 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 107.725 | 600.146 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146