## 170_62U
S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links
Universal and Extra Performance Styles | [9 empty] | Universal and Extra Performance Styles | [9 empty] | Universal and Extra Performance Styles
"T" Speed (TCC 170-6-2) | [9 empty] | "T" Speed (TCC 170-6-2) | [9 empty] | "T" Speed (TCC 170-6-2)
Total Clearing Time-Current Characteristic Curves Dated December 17, 1984 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated December 17, 1984 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated December 17, 1984
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
6T |  | 8T |  | 10T |  | 12T |  | 15T |  | 20T |  | 25T |  | 30T |  | 40T |  | 50T |  | 65T |  | 80T |  | 100T |  | 140T |  | 200T
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
10000 | 0.013512 | 10000 | 0.013512 | 10000 | 0.013512 | 10000 | 0.013512 | 10000 | 0.013512 | 10000 | 0.013662 | 10000 | 0.013896 | 10000 | 0.014219 | 10000 | 0.014667 | 10000 | 0.015342 | 10000 | 0.016753 | 10000 | 0.018627 | 10000 | 0.020524 | 10000 | 0.036364 | 10000 | 0.072428
8025.19 | 0.013526 | 7341.81 | 0.013512 | 6237.53 | 0.013607 | 6831.78 | 0.013526 | 6750.29 | 0.013553 | 8719.7 | 0.013716 | 9075.56 | 0.013951 | 9231.16 | 0.014376 | 9333.26 | 0.014948 | 9550.42 | 0.015574 | 9569.54 | 0.017092 | 9559.97 | 0.019155 | 9617.5 | 0.021234 | 9417.64 | 0.039709 | 9636.76 | 0.076294
6472.65 | 0.013553 | 5471.68 | 0.013553 | 5482.63 | 0.013675 | 5827.48 | 0.01358 | 6120.14 | 0.013675 | 7749.16 | 0.013785 | 8419.79 | 0.014064 | 8386.18 | 0.014564 | 8676.21 | 0.01522 | 8976.27 | 0.015888 | 9021.27 | 0.017559 | 8807.33 | 0.020218 | 9102.82 | 0.022479 | 8641.57 | 0.044772 | 8994.24 | 0.084995
5341.92 | 0.013553 | 3977.23 | 0.013607 | 4657.99 | 0.013771 | 5101.76 | 0.013662 | 5621.42 | 0.013785 | 6935.03 | 0.013924 | 7718.23 | 0.014219 | 7687.42 | 0.014755 | 7929.46 | 0.015574 | 8336.01 | 0.016356 | 8495.91 | 0.018058 | 8294.43 | 0.021022 | 8572.72 | 0.023893 | 8089.64 | 0.049185 | 8344.35 | 0.095736
4210.52 | 0.01358 | 3285.72 | 0.013648 | 4081.99 | 0.01384 | 4593.24 | 0.013771 | 5251.87 | 0.013896 | 6281.35 | 0.014064 | 7075.12 | 0.014391 | 7182.05 | 0.014948 | 7276.03 | 0.015952 | 7679.73 | 0.016905 | 8017.16 | 0.018589 | 7780.22 | 0.022012 | 8073.48 | 0.025447 | 7550.28 | 0.054412 | 7866.28 | 0.10559
3419.81 | 0.013621 | 2961.17 | 0.01373 | 3764.39 | 0.013924 | 4218.94 | 0.013868 | 4906.62 | 0.014021 | 5781.05 | 0.014219 | 6531.16 | 0.014594 | 6723.34 | 0.015174 | 6743.54 | 0.01634 | 7254.23 | 0.017333 | 7542.73 | 0.019251 | 7349.15 | 0.023002 | 7550.28 | 0.027429 | 7089.29 | 0.060135 | 7385.99 | 0.11728
2920 | 0.013662 | 2736.24 | 0.013826 | 3389.17 | 0.014035 | 3961.35 | 0.013979 | 4506.79 | 0.014205 | 5220.46 | 0.014448 | 5933.33 | 0.014844 | 6268.8 | 0.015434 | 6306.53 | 0.01677 | 6804.5 | 0.017843 | 7075.12 | 0.020077 | 6941.96 | 0.024085 | 7153.38 | 0.029271 | 6649.79 | 0.066859 | 7011.73 | 0.12884
2636.85 | 0.013675 | 2546.16 | 0.013882 | 3144.28 | 0.014106 | 3675.12 | 0.01412 | 4168.62 | 0.014391 | 4690.71 | 0.01477 | 5510.11 | 0.015053 | 5886.05 | 0.015683 | 5827.48 | 0.017315 | 6363.54 | 0.018423 | 6610.01 | 0.021001 | 6596.8 | 0.025219 | 6723.34 | 0.031582 | 6256.27 | 0.074261 | 6421.07 | 0.1512
2434.12 | 0.01373 | 2327.01 | 0.014007 | 2925.85 | 0.014205 | 3423.23 | 0.014276 | 3890.68 | 0.014608 | 4317.1 | 0.015008 | 5071.24 | 0.015327 | 5537.73 | 0.015984 | 5499.1 | 0.017771 | 5856.69 | 0.019348 | 6200.22 | 0.0221 | 6126.26 | 0.027237 | 6250.02 | 0.03466 | 5844.99 | 0.083145 | 6010.96 | 0.17133
2148.1 | 0.01384 | 2158.87 | 0.014106 | 2783.15 | 0.014262 | 3156.88 | 0.014477 | 3682.47 | 0.014785 | 3997.16 | 0.015265 | 4630.13 | 0.015667 | 5204.82 | 0.01634 | 5132.46 | 0.018368 | 5488.12 | 0.020198 | 5729.25 | 0.023608 | 5706.38 | 0.029183 | 5862.55 | 0.037811 | 5417.23 | 0.094878 | 5621.42 | 0.19395
1928.2 | 0.013938 | 2000.88 | 0.014248 | 2631.58 | 0.014362 | 2917.09 | 0.014711 | 3454.18 | 0.015008 | 3723.21 | 0.015543 | 4347.43 | 0.015936 | 4887.03 | 0.016803 | 4877.27 | 0.01887 | 5056.05 | 0.021383 | 5363.33 | 0.024993 | 5299.35 | 0.031677 | 5488.12 | 0.041537 | 5035.86 | 0.1073 | 5158.19 | 0.2292
1796.04 | 0.014035 | 1874.95 | 0.014391 | 2456.12 | 0.014492 | 2711.72 | 0.014933 | 3236.8 | 0.01525 | 3362.16 | 0.015984 | 4098.35 | 0.016242 | 4552.08 | 0.017315 | 4584.06 | 0.019699 | 4704.81 | 0.022728 | 5071.24 | 0.026432 | 4843.25 | 0.035114 | 5173.68 | 0.045132 | 4690.71 | 0.12098 | 4681.34 | 0.27661
1674.62 | 0.014148 | 1749.95 | 0.014564 | 2294.66 | 0.014652 | 2475.85 | 0.01525 | 3039.17 | 0.015481 | 3125.47 | 0.016372 | 3871.28 | 0.01657 | 4257.09 | 0.017914 | 4312.79 | 0.020524 | 4347.43 | 0.024254 | 4804.65 | 0.027871 | 4461.95 | 0.038923 | 4833.57 | 0.049829 | 4399.91 | 0.13518 | 4291.28 | 0.32721
1558.28 | 0.014262 | 1634.9 | 0.014726 | 2139.53 | 0.014814 | 2296.96 | 0.015512 | 2867.91 | 0.015699 | 2911.26 | 0.016854 | 3624.02 | 0.01704 | 3969.28 | 0.018552 | 4049.47 | 0.02149 | 4045.42 | 0.025883 | 4426.39 | 0.030374 | 4181.14 | 0.042546 | 4453.03 | 0.05635 | 4156.13 | 0.1485 | 3871.28 | 0.39885
1439.91 | 0.014391 | 1525.9 | 0.014933 | 2018.96 | 0.014963 | 2133.12 | 0.015841 | 2658.03 | 0.016016 | 2730.77 | 0.017333 | 3450.73 | 0.017437 | 3678.79 | 0.019445 | 3817.46 | 0.022547 | 3704.64 | 0.028292 | 4069.76 | 0.033234 | 3871.28 | 0.047446 | 4123.02 | 0.063535 | 3929.79 | 0.16511 | 3595.15 | 0.46619
1346.6 | 0.014535 | 1421.32 | 0.015144 | 1905.2 | 0.015174 | 1994.88 | 0.016145 | 2480.81 | 0.016389 | 2543.61 | 0.01795 | 3246.52 | 0.01795 | 3478.44 | 0.020218 | 3602.34 | 0.023703 | 3443.83 | 0.030587 | 3848.12 | 0.035609 | 3616.78 | 0.052488 | 3817.46 | 0.071851 | 3667.77 | 0.18728 | 3338.71 | 0.54927
1243.07 | 0.014726 | 1338.55 | 0.015388 | 1787.08 | 0.01545 | 1854.44 | 0.016553 | 2338.68 | 0.016753 | 2371.65 | 0.018645 | 3094.37 | 0.018423 | 3259.54 | 0.021107 | 3375.64 | 0.025168 | 3175.88 | 0.033368 | 3577.22 | 0.039001 | 3358.8 | 0.058768 | 3492.39 | 0.082896 | 3365.53 | 0.22087 | 3054.41 | 0.66754
1145.2 | 0.014948 | 1254.31 | 0.015667 | 1674.62 | 0.015778 | 1749.95 | 0.016905 | 2229.07 | 0.01704 | 2215.74 | 0.019542 | 2865.05 | 0.019387 | 3024.01 | 0.022278 | 3144.28 | 0.027101 | 2970.07 | 0.036292 | 3355.45 | 0.042504 | 3122.35 | 0.066062 | 3262.8 | 0.092906 | 3097.47 | 0.25868 | 2842.22 | 0.77946
1052.94 | 0.015265 | 1176.55 | 0.016 | 1585 | 0.016064 | 1659.61 | 0.017298 | 2116.12 | 0.017437 | 2072.15 | 0.020442 | 2698.2 | 0.020198 | 2774.82 | 0.023869 | 2958.21 | 0.028835 | 2785.94 | 0.039511 | 3144.28 | 0.046413 | 2902.54 | 0.07441 | 2859.32 | 0.11623 | 2853.61 | 0.30296 | 2692.81 | 0.87358
954.648 | 0.015652 | 1101.4 | 0.016389 | 1485.25 | 0.016438 | 1572.37 | 0.017718 | 2025.03 | 0.017771 | 1909.01 | 0.021749 | 2495.74 | 0.021297 | 2595 | 0.025269 | 2763.74 | 0.031174 | 2584.64 | 0.043711 | 2946.4 | 0.050886 | 2628.95 | 0.087234 | 2574.32 | 0.14041 | 2650.07 | 0.34848 | 2525.87 | 1.0139
871.611 | 0.016112 | 1018.76 | 0.016837 | 1383.45 | 0.016888 | 1500.18 | 0.018148 | 1905.2 | 0.018313 | 1781.73 | 0.023002 | 2331.67 | 0.022479 | 2409.9 | 0.027129 | 2564.04 | 0.033838 | 2405.08 | 0.04855 | 2730.77 | 0.056974 | 2407.49 | 0.10155 | 2294.66 | 0.1734 | 2463.5 | 0.39965 | 2374.02 | 1.171
797.389 | 0.016586 | 938.556 | 0.017437 | 1277.09 | 0.017454 | 1417.06 | 0.018776 | 1772.84 | 0.019003 | 1659.61 | 0.0244 | 2204.69 | 0.023537 | 2258.24 | 0.02895 | 2400.28 | 0.036656 | 2238 | 0.053979 | 2528.4 | 0.064173 | 2178.39 | 0.1211 | 2082.53 | 0.20594 | 2308.47 | 0.45605 | 2233.53 | 1.3755
739.773 | 0.017092 | 869.869 | 0.018076 | 1199.11 | 0.01795 | 1352 | 0.019309 | 1699.93 | 0.019523 | 1550.51 | 0.026013 | 2109.78 | 0.024449 | 2103.46 | 0.031362 | 2267.29 | 0.039472 | 2057.69 | 0.061657 | 2388.31 | 0.070217 | 2000.88 | 0.14083 | 1882.47 | 0.24779 | 2141.67 | 0.52773 | 2124.6 | 1.5665
702.288 | 0.017489 | 803.794 | 0.018889 | 1113.58 | 0.018571 | 1265.65 | 0.020259 | 1618.64 | 0.020178 | 1450.03 | 0.027815 | 1975.03 | 0.025987 | 1967.15 | 0.033669 | 2103.46 | 0.043623 | 1878.71 | 0.071635 | 2222.39 | 0.079011 | 1834.16 | 0.16494 | 1729.07 | 0.28992 | 2012.92 | 0.59383 | 2006.89 | 1.8401
667.369 | 0.01795 | 749.453 | 0.019699 | 1027.97 | 0.019406 | 1170.68 | 0.021426 | 1525.9 | 0.021001 | 1345.26 | 0.030162 | 1852.59 | 0.027732 | 1874.95 | 0.035644 | 1975.03 | 0.047923 | 1737.74 | 0.081336 | 2020.98 | 0.092443 | 1676.29 | 0.19512 | 1597.73 | 0.33785 | 1890.01 | 0.67223 | 1924.34 | 2.0935
622.251 | 0.018645 | 689.76 | 0.020897 | 971.987 | 0.020057 | 1118.05 | 0.022322 | 1457.3 | 0.02188 | 1230.7 | 0.033334 | 1725.62 | 0.029862 | 1787.08 | 0.037773 | 1871.21 | 0.05181 | 1535.08 | 0.099942 | 1841.51 | 0.10827 | 1552.06 | 0.22466 | 1476.37 | 0.39409 | 1776.39 | 0.76632 | 1837.83 | 2.4153
586.014 | 0.019387 | 647.645 | 0.02199 | 926.434 | 0.02073 | 1069.92 | 0.023233 | 1383.45 | 0.022956 | 1136.08 | 0.036693 | 1594.54 | 0.032511 | 1693.14 | 0.040593 | 1755.2 | 0.057088 | 1357.42 | 0.1233 | 1669.6 | 0.12871 | 1407.17 | 0.26897 | 1357.42 | 0.46294 | 1681.33 | 0.86575 | 1764 | 2.7589
549.134 | 0.020259 | 581.926 | 0.024061 | 875.98 | 0.021598 | 1011.65 | 0.024376 | 1321.26 | 0.023893 | 1072.06 | 0.039789 | 1467.53 | 0.035823 | 1607.35 | 0.043623 | 1634.9 | 0.064045 | 1213.59 | 0.15105 | 1524.37 | 0.15165 | 1312.04 | 0.3057 | 1255.56 | 0.5384 | 1594.54 | 0.97126 | 1696.53 | 3.1608
515.091 | 0.021212 | 529.717 | 0.026195 | 824.142 | 0.02266 | 955.603 | 0.025883 | 1239.35 | 0.025371 | 995.597 | 0.04415 | 1366.95 | 0.039197 | 1500.18 | 0.048163 | 1522.85 | 0.071635 | 1089.35 | 0.18394 | 1386.22 | 0.17922 | 1202.72 | 0.36126 | 1162.51 | 0.62179 | 1495.68 | 1.115 | 1631.64 | 3.5997
477.394 | 0.022502 | 483.158 | 0.028806 | 771.505 | 0.024013 | 887.442 | 0.027843 | 1133.81 | 0.027788 | 930.147 | 0.048842 | 1288.64 | 0.042589 | 1400.16 | 0.053442 | 1402.96 | 0.082071 | 968.107 | 0.22828 | 1274.54 | 0.20947 | 1113.58 | 0.41888 | 1062.46 | 0.74292 | 1393.17 | 1.3097 | 1561.4 | 4.1948
437.617 | 0.024109 | 431.964 | 0.032479 | 732.412 | 0.025244 | 817.575 | 0.030374 | 1049.78 | 0.030223 | 856.062 | 0.05529 | 1196.72 | 0.047304 | 1323.9 | 0.05795 | 1296.39 | 0.093279 | 869 | 0.27855 | 1159.03 | 0.25003 | 1019.78 | 0.498 | 983.721 | 0.86835 | 1313.35 | 1.5066 | 1497.18 | 4.903
406.809 | 0.025805 | 379.306 | 0.038 | 682.896 | 0.02702 | 750.953 | 0.033368 | 969.076 | 0.033135 | 784.733 | 0.063345 | 1110.25 | 0.05291 | 1241.83 | 0.064173 | 1212.38 | 0.10444 | 769.963 | 0.34918 | 1055.04 | 0.29934 | 937.618 | 0.58969 | 892.782 | 1.0638 | 1222.12 | 1.7929 | 1448.58 | 5.5447
375.156 | 0.027899 | 338.1 | 0.04446 | 638.641 | 0.029125 | 685.633 | 0.037285 | 899.953 | 0.036219 | 717.909 | 0.073229 | 1018.76 | 0.060255 | 1159.03 | 0.071707 | 1124.78 | 0.11822 | 685.633 | 0.43511 | 966.173 | 0.35552 | 861.214 | 0.70106 | 825.792 | 1.2559 | 1157.87 | 2.0541 | 1397.36 | 6.3652
347.354 | 0.030132 | 306.845 | 0.051192 | 600.849 | 0.031112 | 632.287 | 0.041579 | 846.697 | 0.039197 | 660.068 | 0.084233 | 947.989 | 0.068006 | 1074.21 | 0.08158 | 1026.94 | 0.13819 | 609.32 | 0.54817 | 842.474 | 0.46248 | 800.585 | 0.81208 | 764.592 | 1.4767 | 1088.26 | 2.4202 | 1350.65 | 7.2561
318.411 | 0.033168 | 276.537 | 0.059835 | 566.424 | 0.033368 | 586.014 | 0.046136 | 800.585 | 0.042546 | 597.852 | 0.099942 | 862.938 | 0.079407 | 986.677 | 0.094405 | 936.681 | 0.16216 | 550.234 | 0.66821 | 766.89 | 0.55479 | 736.82 | 0.96256 | 710.055 | 1.7312 | 1038.3 | 2.7424 | 1297.69 | 8.5066
287.247 | 0.03766 | 249.971 | 0.070217 | 530.778 | 0.036075 | 516.638 | 0.055179 | 755.472 | 0.04609 | 535.576 | 0.1211 | 778.48 | 0.094216 | 914.468 | 0.1074 | 869.869 | 0.18504 | 493.905 | 0.82931 | 685.633 | 0.69408 | 683.58 | 1.1307 | 660.068 | 2.0337 | 992.615 | 3.1014 | 1258.08 | 9.6876
261.215 | 0.042717 | 225.957 | 0.083312 | 498.37 | 0.039432 | 476.917 | 0.062589 | 696.692 | 0.051862 | 486.065 | 0.14368 | 710.766 | 0.11001 | 854.352 | 0.12049 | 800.585 | 0.21521 | 450.043 | 1.0008 | 626.622 | 0.83097 | 632.919 | 1.3309 | 631.023 | 2.2633 | 957.516 | 3.4585 | 1218.45 | 11.0435
240.891 | 0.047923 | 203.434 | 0.099842 | 460.054 | 0.044106 | 434.999 | 0.072283 | 641.843 | 0.058474 | 434.999 | 0.17584 | 656.12 | 0.12591 | 798.187 | 0.13572 | 736.083 | 0.25179 | 415.027 | 1.1827 | 576.136 | 0.97808 | 591.903 | 1.5432 | 599.648 | 2.5443 | 932.009 | 3.7767 | 1177.72 | 12.7412
218.403 | 0.055345 | 185.183 | 0.11787 | 412.544 | 0.051603 | 386.582 | 0.087234 | 588.951 | 0.066459 | 393.997 | 0.20968 | 583.674 | 0.15456 | 719.346 | 0.1633 | 676.778 | 0.29489 | 386.195 | 1.3755 | 530.247 | 1.1605 | 552.439 | 1.7875 | 572.117 | 2.8401 | 901.755 | 4.2116 | 1145.2 | 14.4233
199.008 | 0.063662 | 166.225 | 0.14225 | 374.033 | 0.059715 | 344.586 | 0.10591 | 537.185 | 0.076753 | 358.29 | 0.25003 | 538.261 | 0.17975 | 664.705 | 0.18992 | 629.763 | 0.33785 | 357.574 | 1.6304 | 480.267 | 1.4174 | 521.831 | 2.0377 | 545.304 | 3.2054 | 878.612 | 4.6406 | 1122.53 | 15.9721
181.879 | 0.073522 | 147.134 | 0.17619 | 326.472 | 0.074484 | 307.152 | 0.13001 | 491.933 | 0.088375 | 322.577 | 0.30448 | 492.918 | 0.21073 | 607.494 | 0.22534 | 569.833 | 0.40895 | 336.414 | 1.8717 | 443.786 | 1.6584 | 488.991 | 2.3581 | 521.831 | 3.5781 | 856.062 | 5.1492 | 1102.5 | 17.7404
166.724 | 0.08508 | 132.866 | 0.21264 | 290.715 | 0.090885 | 272.147 | 0.16087 | 450.493 | 0.10227 | 290.715 | 0.36745 | 444.23 | 0.25611 | 554.099 | 0.26682 | 521.831 | 0.48328 | 319.687 | 2.0977 | 410.897 | 1.9539 | 460.054 | 2.7342 | 498.37 | 4.0182 | 837.434 | 5.6964 | 1079.59 | 20.1226
152.527 | 0.099245 | 116.203 | 0.27578 | 259.652 | 0.11023 | 238.732 | 0.2045 | 403.971 | 0.12379 | 259.133 | 0.4565 | 386.195 | 0.33382 | 495.885 | 0.32819 | 477.394 | 0.56998 | 305.01 | 2.351 | 385.809 | 2.2341 | 435.87 | 3.12 | 476.441 | 4.5624 | 824.967 | 6.1709 | 1060.33 | 22.2835
139.958 | 0.11577 | 104.725 | 0.34022 | 230.291 | 0.13545 | 214.722 | 0.24953 | 364.433 | 0.14924 | 234.005 | 0.55479 | 334.736 | 0.43424 | 454.112 | 0.38862 | 440.25 | 0.67021 | 286.673 | 2.7233 | 362.978 | 2.5545 | 417.942 | 3.4689 | 455.932 | 5.1287 | 804.598 | 6.9022 | 1035.19 | 25.6834
128.425 | 0.13477 | 89.3307 | 0.469 | 209.839 | 0.15943 | 197.817 | 0.29137 | 330.413 | 0.17868 | 214.507 | 0.65694 | 298.074 | 0.5449 | 412.132 | 0.47087 | 398.753 | 0.8186 | 273.238 | 3.0705 | 343.21 | 2.8888 | 402.761 | 3.8261 | 434.13 | 5.9053 | 788.666 | 7.7202 | 1015.71 | 28.584
115.393 | 0.16297 | 78.3625 | 0.61008 | 190.061 | 0.19106 | 179.171 | 0.34953 | 302.882 | 0.21243 | 197.817 | 0.77557 | 269.979 | 0.6609 | 383.885 | 0.54326 | 372.167 | 0.93973 | 260.432 | 3.4793 | 327.453 | 3.1958 | 386.195 | 4.271 | 417.107 | 6.6051 | 770.734 | 8.8538 | 997.59 | 31.4012
106.627 | 0.18746 | 69.0165 | 0.79839 | 174.922 | 0.2222 | 161.959 | 0.42309 | 270.249 | 0.26259 | 183.157 | 0.9065 | 241.856 | 0.82353 | 352.603 | 0.64522 | 342.524 | 1.1139 | 250.221 | 3.8723 | 310.549 | 3.5997 | 368.096 | 4.8542 | 403.567 | 7.2998 | 754.717 | 10.225 | 980.775 | 34.0846
99.1214 | 0.21564 | 63.7103 | 0.95013 | 159.229 | 0.26603 | 147.871 | 0.50552 | 242.34 | 0.32298 | 171.459 | 1.0448 | 217.097 | 1.0221 | 322.9 | 0.77557 | 314.613 | 1.3282 | 240.409 | 4.3053 | 296.884 | 4.0022 | 350.144 | 5.5892 | 390.077 | 8.1404 | 739.773 | 11.6796 | 967.14 | 36.7393
91.5922 | 0.25078 | 57.9944 | 1.1722 | 146.107 | 0.31564 | 133.933 | 0.6113 | 217.749 | 0.39686 | 156.858 | 1.2584 | 195.067 | 1.2761 | 295.699 | 0.92759 | 290.715 | 1.5712 | 230.291 | 4.8785 | 286.96 | 4.4187 | 329.094 | 6.559 | 375.908 | 9.2613 | 726.576 | 13.2745 | 943.261 | 41.1345
85.4 | 0.28876 | 52.1616 | 1.4812 | 130.888 | 0.39135 | 122.651 | 0.72749 | 200.405 | 0.46759 | 142.643 | 1.5324 | 177.211 | 1.5556 | 272.147 | 1.1116 | 269.709 | 1.8494 | 218.84 | 5.6511 | 275.984 | 4.9177 | 316.823 | 7.3364 | 364.798 | 10.3381 | 711.477 | 15.5622 | 923.659 | 45.3698
79.1501 | 0.33549 | 47.6244 | 1.831 | 119.145 | 0.46853 | 112.995 | 0.85457 | 179.889 | 0.57859 | 132.733 | 1.7875 | 159.867 | 1.9403 | 245.511 | 1.3907 | 255.02 | 2.0935 | 211.737 | 6.283 | 267.025 | 5.4567 | 307.767 | 8.0514 | 354.371 | 11.6679 | 698.086 | 17.865 | 899.054 | 51.1032
73.211 | 0.39252 | 42.6636 | 2.344 | 108.456 | 0.56374 | 105.99 | 0.9732 | 162.283 | 0.71379 | 125.63 | 2.0215 | 148.167 | 2.2929 | 222.815 | 1.7295 | 244.287 | 2.323 | 205.684 | 6.9299 | 259.133 | 6.079 | 299.868 | 8.8184 | 345.621 | 13.0507 | 685.633 | 19.8826 | 873.356 | 58.1397
68.4666 | 0.45106 | 40.4613 | 2.6667 | 95.2348 | 0.73186 | 98.6271 | 1.1318 | 145.233 | 0.89122 | 120.342 | 2.2207 | 136.502 | 2.7617 | 205.684 | 2.0727 | 230.752 | 2.6481 | 199.207 | 7.8134 | 252.23 | 6.7116 | 290.424 | 9.9229 | 336.751 | 14.7146 | 676.101 | 21.6249 | 853.498 | 63.9978
63.774 | 0.52196 | 37.9909 | 3.0952 | 85.1442 | 0.91836 | 90.9533 | 1.3349 | 132.733 | 1.067 | 115.162 | 2.4567 | 128.296 | 3.2054 | 190.061 | 2.4864 | 221.261 | 2.9325 | 193.9 | 8.7132 | 246.003 | 7.4622 | 281.278 | 11.2891 | 327.78 | 16.6739 | 658.749 | 24.7257 | 833.258 | 70.7993
59.4031 | 0.60281 | 35.9578 | 3.5354 | 79.7061 | 1.049 | 81.8875 | 1.6767 | 123.142 | 1.2421 | 110.315 | 2.7178 | 117.96 | 3.9545 | 176.504 | 2.9738 | 213.224 | 3.2086 | 187.418 | 9.913 | 238.971 | 8.4136 | 273.511 | 12.7923 | 320.007 | 18.8374 | 645.06 | 27.8504 | 809.44 | 79.9858
55.2764 | 0.69966 | 34.0335 | 4.0343 | 74.4662 | 1.2066 | 75.3652 | 2.0154 | 111.535 | 1.5355 | 104.83 | 3.0644 | 110.205 | 4.7533 | 164.242 | 3.5425 | 204.454 | 3.5638 | 182.243 | 11.2553 | 233.304 | 9.4201 | 265.693 | 14.6706 | 312.418 | 21.2604 | 629.133 | 31.7485 | 788.666 | 88.6636
51.3336 | 0.81533 | 32.0836 | 4.6779 | 70.1297 | 1.3659 | 71.0473 | 2.316 | 103.787 | 1.784 | 99.2206 | 3.4828 | 103.787 | 5.5669 | 153.445 | 4.22 | 195.653 | 3.9902 | 177.211 | 12.8307 | 227.316 | 10.6317 | 259.133 | 16.6572 | 305.315 | 24.2361 | 615.443 | 35.5467 | 766.123 | 99.3699
48.055 | 0.93879 | 29.7952 | 5.6341 | 64.7378 | 1.6094 | 65.9796 | 2.7534 | 96.9646 | 2.0685 | 94.3816 | 3.9545 | 100.518 | 6.0608 | 145.233 | 4.8981 | 187.606 | 4.4765 | 173.182 | 14.4088 | 221.926 | 11.9394 | 251.475 | 19.5279 | 299.569 | 27.3809 | 604.465 | 39.0502 | 741.995 | 112.039
44.851 | 1.0907 | 27.6976 | 6.7049 | 60.1804 | 1.8792 | 62.4487 | 3.164 | 90.7715 | 2.3889 | 89.3307 | 4.5396 | 96.0958 | 7.0136 | 138.982 | 5.5447 | 180.43 | 4.9424 | 168.737 | 16.6406 | 217.097 | 13.3277 | 246.742 | 21.7768 | 292.464 | 31.9077 | 591.312 | 43.8093 | 720.066 | 124.318
42.2391 | 1.2384 | 26.3204 | 7.6894 | 55.3871 | 2.2363 | 57.8785 | 3.8299 | 84.974 | 2.7755 | 84.7195 | 5.2166 | 92.9764 | 7.8526 | 133.132 | 6.2704 | 172.836 | 5.5836 | 164.407 | 19.3336 | 211.525 | 15.3919 | 240.169 | 25.4024 | 287.247 | 36.3374 | 579.603 | 48.5138 | 698.785 | 136.982
39.9387 | 1.4061 | 25.2379 | 8.6785 | 51.9014 | 2.5621 | 54.7264 | 4.4453 | 80.1858 | 3.1735 | 80.9916 | 5.8524 | 90.1384 | 8.7832 | 127.401 | 7.1552 | 167.728 | 6.1278 | 159.867 | 22.9391 | 205.684 | 18.0085 | 234.708 | 29.8101 | 281.559 | 41.5895 | 565.292 | 54.5898 | 682.214 | 147.503
37.1642 | 1.6419 | 24.224 | 9.8833 | 48.1994 | 3.043 | 52.528 | 4.9671 | 76.5042 | 3.5532 | 76.8108 | 6.7995 | 87.6495 | 9.8537 | 122.651 | 8.1079 | 163.26 | 6.6582 | 156.545 | 26.3336 | 200.606 | 21.0068 | 230.752 | 34.2212 | 275.984 | 48.031 | 552.439 | 60.8157 | 666.702 | 159.948
34.5479 | 1.9345 | 23.4143 | 11.1992 | 45.0308 | 3.5425 | 50.2669 | 5.6116 | 72.9188 | 4.0022 | 73.6516 | 7.7125 | 85.4854 | 10.9445 | 118.432 | 8.9428 | 157.802 | 7.4921 | 153.138 | 30.5647 | 195.262 | 25.1748 | 226.183 | 39.9987 | 271.875 | 54.9184 | 538.799 | 68.4326 | 650.892 | 174.487
32.4061 | 2.2431 | 22.7905 | 12.4889 | 42.5358 | 4.0586 | 48.055 | 6.4485 | 69.3625 | 4.5305 | 70.6223 | 8.7482 | 83.3748 | 12.3276 | 114.702 | 9.8635 | 152.985 | 8.4388 | 150.708 | 34.8777 | 191.779 | 28.6412 | 222.148 | 46.4719 | 267.025 | 63.6786 | 524.446 | 77.0034 | 636.728 | 192.068
30.2757 | 2.6035 | 22.2278 | 14.237 | 40.3805 | 4.6036 | 46.2632 | 7.2489 | 66.4431 | 5.0776 | 67.7176 | 10.0326 | 81.3162 | 13.7886 | 110.647 | 11.3117 | 148.316 | 9.5816 | 147.871 | 40.6845 | 188.924 | 32.1639 | 218.185 | 55.2489 | 263.313 | 71.9412 | 509.456 | 85.7854 | 626.622 | 208.065
28.5983 | 2.9768 | 21.6141 | 16.9598 | 37.5002 | 5.5447 | 44.1391 | 8.4473 | 63.3925 | 5.7883 | 65.0623 | 11.5057 | 79.7061 | 15.3458 | 107.269 | 13.0116 | 144.22 | 10.8032 | 145.233 | 46.5649 | 185.925 | 36.776 | 215.582 | 63.7423 | 258.874 | 84.2551 | 491.933 | 97.6949 | 616.676 | 227.204
26.7985 | 3.4793 | 21.0383 | 20.0623 | 35.0349 | 6.5919 | 42.749 | 9.4107 | 60.846 | 6.4549 | 63.2026 | 12.9597 | 78.0497 | 17.1817 | 104.516 | 14.818 | 138.565 | 13.0246 | 142.928 | 53.402 | 182.426 | 42.3025 | 212.373 | 75.3278 | 254.765 | 98.6768 | 477.394 | 108.51 | 608.711 | 249.847
25.0869 | 4.0263 | 20.5805 | 23.6141 | 33.4264 | 7.5071 | 41.6935 | 10.3072 | 58.5187 | 7.2852 | 61.4575 | 14.5682 | 76.275 | 19.6062 | 100.82 | 17.5288 | 135.009 | 14.6412 | 140.8 | 61.2429 | 179.53 | 48.1754 | 209.63 | 86.1293 | 251.224 | 114.188 | 461.436 | 121.857 | 600.849 | 273.924
23.7206 | 4.599 | 20.2134 | 27.7114 | 31.9236 | 8.5322 | 40.8271 | 11.3344 | 55.7761 | 8.4052 | 59.9401 | 16.3928 | 74.69 | 22.128 | 98.6271 | 20.0223 | 132.071 | 16.4421 | 138.843 | 69.6755 | 176.68 | 57.7341 | 206.922 | 102.293 | 247.979 | 131.348 | 445.565 | 136.026 | 594.87 | 310.707
22.5187 | 5.2427 | 19.8528 | 33.8807 | 31.0111 | 9.3357 | 39.8589 | 12.539 | 54.0195 | 9.2428 | 58.7532 | 18.4644 | 73.5044 | 24.627 | 96.2882 | 23.4025 | 129.197 | 18.5755 | 136.913 | 78.5589 | 174.224 | 66.0128 | 204.045 | 121.128 | 244.531 | 152.299 | 432.397 | 148.836 | 588.951 | 359.549
21.4419 | 5.9586 | 19.4987 | 41.5895 | 30.0645 | 10.4212 | 39.1479 | 13.997 | 52.0053 | 10.463 | 57.4173 | 20.9229 | 72.4826 | 26.9463 | 94.3816 | 27.4357 | 125.882 | 21.755 | 134.874 | 91.5467 | 170.945 | 80.2261 | 201.008 | 146.181 | 241.373 | 179.262 | 419.198 | 164.984 | 585.428 | 413.167
20.6217 | 6.6051 | 19.1508 | 52.3445 | 29.2929 | 11.5634 | 38.296 | 15.7658 | 50.3172 | 11.7616 | 56.3931 | 23.6614 | 70.9054 | 32.0355 | 92.1434 | 33.2763 | 122.528 | 25.9415 | 132.733 | 107.109 | 168.906 | 91.2725 | 198.809 | 173.096 | 238.494 | 203.131 | 408.848 | 181.426 | 583.091 | 473.358
20.1327 | 7.0487 | 18.8657 | 64.2543 | 28.6269 | 12.9079 | 37.2014 | 18.5569 | 48.6838 | 13.6514 | 55.166 | 27.3535 | 69.5013 | 37.444 | 90.2285 | 39.8789 | 119.862 | 30.3212 | 131.15 | 121.37 | 166.391 | 106.043 | 195.849 | 210.366 | 236.121 | 231.794 | 398.753 | 202.928 | 580.763 | 539.074
19.4597 | 7.7978 | 18.6593 | 77.8551 | 28.004 | 14.3657 | 36.4283 | 20.9858 | 47.7198 | 15.2083 | 54.1819 | 31.3385 | 68.4666 | 43.5038 | 88.5304 | 46.892 | 117.606 | 34.7384 | 129.197 | 141.295 | 163.914 | 128.105 | 194.288 | 238.853 | 233.771 | 263.71 | 391.249 | 225.619 | 578.445 | 603.565
18.8468 | 8.5749 | 18.3999 | 99.4694 | 27.4769 | 16.1973 | 35.6713 | 24.043 | 46.4486 | 17.599 | 53.2153 | 36.4101 | 67.3125 | 50.6454 | 86.6906 | 56.5909 | 114.932 | 41.7562 | 127.529 | 162.528 | 161.151 | 152.757 | 192.74 | 273.924 | 232.373 | 283.965 | 386.968 | 249.598
18.3815 | 9.2984 | 18.3265 | 122.223 | 26.9328 | 18.5755 | 34.9649 | 27.9061 | 45.3018 | 20.1831 | 52.4755 | 42.0075 | 66.3767 | 59.3142 | 85.1442 | 69.2587 | 112.207 | 51.7719 | 125.882 | 185.833 | 159.229 | 179.621 | 191.396 | 299.721 | 231.214 | 302.43 | 383.885 | 278.064
17.9456 | 10.0829 | 18.2168 | 149.433 | 26.3731 | 21.3669 | 34.3756 | 31.5902 | 44.2275 | 23.5669 | 51.6942 | 48.9524 | 65.3885 | 69.9548 | 83.7927 | 82.5042 | 109.546 | 63.9338 | 124.505 | 211.209 | 157.802 | 206.201 |  |  |  |  | 381.207 | 318.892
17.5551 | 10.9665 | 18.1804 | 187.701 | 25.9545 | 24.3333 | 33.7286 | 37.1456 | 43.3951 | 26.5717 | 51.1287 | 55.7484 | 64.7378 | 80.0658 | 82.4627 | 98.4796 | 107.591 | 76.0088 | 123.266 | 236.95 | 156.076 | 236.004 |  |  |  |  | 378.17 | 375.347
17.0875 | 12.2907 | 18.1804 | 224.719 | 25.5937 | 27.7669 | 33.2264 | 44.2939 | 42.4508 | 31.3385 | 50.5694 | 66.7429 | 64.0937 | 92.9303 | 81.3162 | 115.451 | 105.461 | 93.5831 | 122.161 | 266.894 | 154.06 | 275.848 |  |  |  |  | 375.532 | 444.012
16.7324 | 13.5156 | 18.1623 | 263.447 | 25.2884 | 32.1318 | 32.7318 | 51.9275 | 41.5271 | 38.2386 | 50.1163 | 79.4278 | 63.3292 | 107.861 | 80.1858 | 139.052 | 103.787 | 110.924 | 121.309 | 287.393 | 152.832 | 302.128 |  |  |  |  | 374.407 | 493.663
16.2541 | 15.5 | 18.0898 | 302.128 | 24.9868 | 37.1085 | 32.309 | 60.7549 | 40.7863 | 46.0095 | 49.5185 | 94.7128 | 62.699 | 121.735 | 78.913 | 169.161 | 102.549 | 127.338 | 120.825 | 303.642 | [6 empty] | 373.285 | 570.124
15.8845 | 17.5814 |  |  | 24.664 | 45.2339 | 31.9236 | 72.6642 | 40.0587 | 55.7484 | 48.9768 | 112.713 | 62.0752 | 142.003 | 77.9717 | 204.967 | 101.123 | 150.483 | [8 empty] | 372.912 | 607.805
15.6637 | 19.3336 |  |  | 24.443 | 53.5089 | 31.4483 | 87.8692 | 39.4623 | 69.3973 | 48.5865 | 130.562 | 61.3347 | 168.149 | 77.1187 | 240.291 | 99.8177 | 176.24
15.4923 | 21.4955 |  |  | 24.1515 | 65.356 | 31.1978 | 104.256 | 38.9526 | 82.5042 | 48.2959 | 147.061 | 60.7244 | 193.031 | 76.4278 | 276.4 | 98.7257 | 205.789
15.3229 | 24.6517 |  |  | 23.959 | 78.2453 | 30.8256 | 128.361 | 38.565 | 99.7682 | 47.959 | 173.096 | 60.1804 | 219.39 | 75.9706 | 301.826 | 97.5481 | 240.531
15.1249 | 28.987 |  |  | 23.7444 | 93.6767 | 30.5494 | 150.633 | 38.1813 | 122.345 | 47.5768 | 200.507 | 59.8204 | 242.463 |  |  | 96.5775 | 278.621
14.9147 | 35.3694 |  |  | 23.626 | 119.205 | 30.2757 | 178.546 | 37.915 | 147.946 | 47.3869 | 232.956 | 59.4031 | 273.924 |  |  | 96.0958 | 301.223
14.6779 | 44.2496 |  |  | 23.5787 | 140.871 | 30.0345 | 211.421 | 37.6882 | 173.27 | 47.0564 | 265.297 | 59.2251 | 301.223
14.5028 | 52.8706 |  |  | 23.5316 | 173.096 | 29.7654 | 250.598 | 37.4627 | 209.946 | 46.9154 | 287.393
14.3012 | 67.0104 |  |  | 23.4846 | 213.119 | 29.6169 | 281.139 | 37.2759 | 236.95 | 46.8217 | 300.321
14.1589 | 84.9319 |  |  | 23.4377 | 248.353 | 29.5873 | 303.642 | 37.2014 | 272.013
14.0883 | 102.601 |  |  | 23.4377 | 280.578 |  |  | 37.1642 | 300.621
14.0461 | 126.703 |  |  | 23.3909 | 302.43
14.0321 | 157.567
13.99 | 196.144
13.9342 | 234.592
13.8786 | 277.508
13.8786 | 300.021