## 170-6
S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links
Universal and Extra-Performance Styles | [9 empty] | Universal and Extra-Performance Styles | [9 empty] | Universal and Extra-Performance Styles
"T" Speed (TCC 170-6) | [9 empty] | "T" Speed (TCC 170-6) | [9 empty] | "T" Speed (TCC 170-6)
Minimum Melting Time-Current Characteristic Curves Dated December 17, 1984 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated December 17, 1984 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated December 17, 1984
Tolerance in Terms of Current: |  |  | Plus 10% for fuse links rated 6T through 100T | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse links rated 6T through 100T | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse links rated 6T through 100T
|  |  | Plus 20% for fuse links rated 140T and 200T | [9 empty] | Plus 20% for fuse links rated 140T and 200T | [9 empty] | Plus 20% for fuse links rated 140T and 200T
6T |  | 8T |  | 10T |  | 12T |  | 15T |  | 20T |  | 25T |  | 30T |  | 40T |  | 50T |  | 65T |  | 80T |  | 100T |  | 140T |  | 200T
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
12.0293 | 298.5244 | 15.7108 | 296.7387 | 20.2135 | 300.9223 | 27.0408 | 298.2262 | 33.7624 | 299.122 | 42.4508 | 300.3211 | 53.4821 | 300.6214 | 68.8098 | 298.2262 | 86.5174 | 298.8232 | 109.3273 | 299.4214 | 138.7044 | 299.122 | 174.3989 | 300.0208 | 209.0022 | 300.0208 | 307.4599 | 608.4127 | 480.2678 | 609.0217
12.0414 | 277.7863 | 15.7265 | 274.1983 | 20.2945 | 265.2974 | 27.095 | 251.3513 | 33.7624 | 281.7026 | 42.4508 | 272.5582 | 54.0196 | 258.7473 | 69.4319 | 262.9205 | 86.9511 | 278.8996 | 109.9852 | 280.8587 | 139.1212 | 285.1035 | 175.624 | 265.8285 | 210.681 | 267.9638 | 307.7675 | 544.4921 | 481.2294 | 557.1604
12.0655 | 245.8819 | 15.758 | 246.128 | 20.3351 | 233.8901 | 27.2035 | 216.7731 | 33.8977 | 246.6207 | 42.621 | 242.7063 | 54.5625 | 221.595 | 70.1999 | 223.5983 | 87.6495 | 252.3587 | 110.6471 | 260.5649 | 139.6788 | 265.8285 | 176.6809 | 237.6624 | 212.5857 | 242.4636 | 308.6921 | 498.6244 | 483.1581 | 508.697
12.1138 | 206.6136 | 15.8054 | 218.5143 | 20.3962 | 202.1179 | 27.3399 | 183.2499 | 33.9995 | 214.4017 | 42.8346 | 208.6902 | 55.0007 | 188.642 | 70.9054 | 191.3015 | 88.3535 | 226.0716 | 111.6474 | 232.491 | 140.5194 | 236.2408 | 177.7442 | 210.1562 | 214.5075 | 216.99 | 309.3102 | 449.3729 | 485.58 | 446.2383
12.1867 | 171.5459 | 15.8687 | 190.7285 | 20.5189 | 162.3656 | 27.4769 | 154.2926 | 34.1358 | 180.5216 | 43.1355 | 175.5371 | 55.5535 | 160.1083 | 72.049 | 157.4094 | 89.0632 | 203.9452 | 113.2215 | 197.7198 | 141.9316 | 211.421 | 179.1718 | 181.9716 | 217.0972 | 186.3918 | 310.5499 | 401.759 | 488.5022 | 396.1736
12.2723 | 147.0614 | 15.9323 | 163.9974 | 20.5806 | 133.333 | 27.8087 | 123.4517 | 34.3069 | 149.284 | 43.482 | 145.1619 | 56.168 | 136.1626 | 72.9917 | 134.8079 | 90.4092 | 167.981 | 114.9326 | 168.9918 | 143.5015 | 184.9066 | 181.1535 | 155.8432 | 219.718 | 161.233 | 312.7314 | 342.3565 | 491.442 | 346.8361
12.3215 | 127.7212 | 16.0122 | 140.7309 | 20.7459 | 108.0776 | 28.0881 | 100.7709 | 34.5134 | 124.8172 | 43.8312 | 121.8572 | 56.7892 | 117.1963 | 73.7991 | 115.1056 | 91.5922 | 143.8614 | 116.5529 | 143.574 | 145.3792 | 157.2522 | 182.9742 | 133.4665 | 223.2617 | 137.2563 | 315.2432 | 300.9223 | 494.3995 | 303.3394
12.3709 | 113.8464 | 16.1085 | 121.7355 | 20.829 | 92.5593 | 28.5412 | 79.1107 | 34.8603 | 101.276 | 44.316 | 100.7709 | 57.4174 | 98.5782 | 74.7647 | 97.6949 | 92.8835 | 121.3708 | 118.4328 | 120.6447 | 147.724 | 130.5622 | 184.998 | 115.7983 | 226.4094 | 119.4443 | 317.4576 | 274.4727 | 497.8725 | 268.2317
12.4205 | 97.7927 | 16.1893 | 105.4091 | 20.9753 | 75.5541 | 28.8857 | 66.8097 | 35.1754 | 82.8349 | 44.7614 | 87.0819 | 58.0524 | 85.0168 | 75.743 | 84.1709 | 94.2873 | 103.2186 | 120.5839 | 100.0679 | 150.2567 | 108.294 | 187.0442 | 100.4691 | 230.0611 | 102.0895 | 319.0489 | 253.6237 | 501.3698 | 244.1667
12.5077 | 84.9318 | 16.3193 | 90.6358 | 21.1438 | 64.2543 | 29.2637 | 56.14 | 35.7427 | 66.6762 | 45.3471 | 75.9328 | 58.8709 | 72.8097 | 76.7341 | 71.1542 | 95.9038 | 86.2154 | 123.2661 | 81.9287 | 152.8329 | 90.999 | 188.924 | 88.4864 | 233.0714 | 89.6443 | 321.2901 | 233.4228 | 509.4562 | 219.39
12.5956 | 73.3945 | 16.4504 | 78.2453 | 21.3777 | 54.1549 | 29.7357 | 46.4719 | 36.102 | 57.1596 | 45.9405 | 63.9338 | 59.522 | 63.1081 | 77.8938 | 61.4884 | 97.5481 | 72.2295 | 125.3795 | 69.6755 | 155.2979 | 76.7727 | 191.5876 | 75.6297 | 236.8305 | 77.1575 | 324.5191 | 216.7731 | 518.7094 | 198.9098
12.6841 | 65.356 | 16.5825 | 68.1594 | 21.6574 | 45.5517 | 30.306 | 38.5844 | 36.5378 | 48.8546 | 46.7749 | 52.7123 | 60.1804 | 54.8635 | 78.8341 | 53.9387 | 99.3199 | 61.0595 | 127.9124 | 57.9656 | 158.1186 | 64.1259 | 193.9005 | 65.8151 | 239.9294 | 68.1594 | 328.1085 | 201.9158 | 527.0756 | 186.5784
12.8372 | 56.4214 | 16.7324 | 60.8157 | 22.0287 | 37.8582 | 30.8565 | 33.0112 | 37.0529 | 42.3449 | 47.3396 | 45.78 | 61.151 | 47.4581 | 80.0256 | 46.3791 | 101.225 | 51.1544 | 130.7577 | 47.9351 | 161.3128 | 53.9926 | 197.0278 | 56.4779 | 243.5555 | 59.6711 | 333.734 | 186.9519 | 542.5845 | 166.8092
13.0052 | 48.6595 | 16.9006 | 52.765 | 22.384 | 32.3252 | 31.4798 | 27.8504 | 37.8014 | 35.3694 | 48.007 | 38.9332 | 62.324 | 40.6032 | 81.235 | 40.4411 | 102.8576 | 44.9184 | 133.6662 | 40.159 | 164.7362 | 44.9184 | 199.8056 | 49.8914 | 247.4837 | 52.6596 | 341.4989 | 170.5196 | 558.5497 | 151.8435
13.149 | 43.1571 | 17.1389 | 45.7343 | 22.8591 | 27.3536 | 32.1158 | 23.971 | 38.4496 | 30.7179 | 48.6838 | 33.6444 | 63.3925 | 35.0876 | 82.5452 | 35.9399 | 104.5166 | 39.3638 | 136.9129 | 33.5772 | 168.0641 | 38.2004 | 202.8253 | 43.2868 | 250.4714 | 46.565 | 350.144 | 157.8824 | 576.136 | 137.9444
13.2679 | 38.5458 | 17.3805 | 39.2852 | 23.3675 | 23.3092 | 32.9617 | 20.386 | 39.3441 | 26.1238 | 49.717 | 28.3279 | 64.4794 | 30.4427 | 84.1286 | 31.2134 | 106.628 | 33.8808 | 139.9585 | 28.8713 | 171.6307 | 32.164 | 205.8906 | 37.8204 | 253.2418 | 41.8398 | 359.3671 | 145.7439 | 596.0615 | 122.836
13.4012 | 34.0846 | 17.6255 | 34.7037 | 23.9351 | 19.9424 | 33.6949 | 17.8472 | 40.0988 | 22.9621 | 50.7213 | 24.6517 | 65.8478 | 26.0455 | 85.5709 | 27.6285 | 108.5647 | 29.6022 | 143.5015 | 24.212 | 175.273 | 27.2716 | 210.26 | 31.8758 | 258.0994 | 36.5927 | 371.0528 | 131.7426 | 614.2142 | 110.3713
13.5495 | 30.17 | 17.874 | 30.9647 | 24.3455 | 17.9187 | 34.6171 | 15.4846 | 41.1551 | 19.5084 | 51.8496 | 21.5386 | 67.3799 | 22.5977 | 87.2124 | 24.309 | 110.6471 | 25.9156 | 147.2814 | 20.5908 | 178.8138 | 23.4494 | 214.2932 | 27.8225 | 263.5768 | 31.6851 | 383.1185 | 119.5638 | 632.9198 | 99.1714
13.6994 | 26.5186 | 18.0537 | 27.9062 | 24.8125 | 16.0041 | 35.6001 | 13.4213 | 42.1547 | 16.9598 | 53.1621 | 18.6314 | 68.741 | 19.9623 | 88.5304 | 21.8422 | 113.2215 | 22.3952 | 152.0707 | 16.8752 | 183.1573 | 19.9623 | 218.1853 | 24.4308 | 267.8279 | 28.6986 | 393.2101 | 109.273 | 653.5007 | 87.8692
13.8509 | 23.4964 | 18.3816 | 24.6764 | 25.4406 | 14.166 | 36.7577 | 11.5057 | 43.569 | 14.4811 | 54.3991 | 16.4421 | 70.1297 | 17.8472 | 90.4092 | 19.353 | 115.6242 | 19.4889 | 156.5453 | 14.5537 | 186.6705 | 17.6167 | 222.593 | 21.7768 | 273.2384 | 25.6065 | 405.1852 | 98.6767 | 675.426 | 77.3894
14.0462 | 20.9439 | 18.6594 | 22.2835 | 26.1108 | 12.7158 | 37.953 | 10.0829 | 45.0308 | 12.464 | 56.2242 | 13.997 | 71.8332 | 15.8449 | 91.9593 | 17.2678 | 118.6699 | 16.8921 | 161.3128 | 12.6777 | 190.632 | 15.5778 | 228.6848 | 18.8186 | 280.1555 | 22.2168 | 417.9427 | 88.6636 | 691.1408 | 70.3758
14.2442 | 18.6873 | 19.0173 | 19.5866 | 26.9598 | 11.2104 | 39.2263 | 8.916 | 46.8685 | 10.7279 | 58.2851 | 12.1928 | 73.6516 | 14.0251 | 93.7232 | 15.3766 | 122.8969 | 14.237 | 167.7283 | 10.653 | 195.0674 | 13.6378 | 234.0055 | 16.6406 | 287.2477 | 19.4305 | 430.2404 | 79.5869 | 710.0557 | 63.2344
14.445 | 16.909 | 19.4403 | 17.2678 | 27.7809 | 9.9926 | 40.4613 | 8.0112 | 48.7813 | 9.4013 | 60.6031 | 10.6424 | 75.5917 | 12.2907 | 95.9038 | 13.8301 | 126.6396 | 12.3153 | 173.0092 | 9.3077 | 199.8056 | 12.0473 | 240.8911 | 14.3945 | 296.2917 | 16.909 | 440.6911 | 71.5824 | 728.7593 | 56.9885
14.7221 | 15.1477 | 19.9125 | 15.1174 | 28.5412 | 9.1691 | 41.9864 | 7.0982 | 51.1287 | 8.0675 | 62.8874 | 9.4484 | 77.8159 | 10.7171 | 98.2334 | 12.3647 | 130.7577 | 10.6318 | 178.1 | 8.1731 | 205.8906 | 10.4944 | 247.4837 | 12.665 | 305.0099 | 14.7736 | 451.8472 | 63.4878 | 744.9695 | 51.7719
15.0045 | 13.7749 | 20.3351 | 13.7749 | 29.617 | 8.2305 | 43.482 | 6.3652 | 53.5891 | 7.0065 | 65.1275 | 8.4388 | 79.8657 | 9.5912 | 100.9218 | 11.11 | 136.3664 | 8.9517 | 183.8913 | 7.2561 | 210.681 | 9.345 | 254.0027 | 11.3799 | 313.0442 | 13.1162 | 465.1426 | 56.0838 | 760.7794 | 46.7984
15.3229 | 12.4515 | 20.7666 | 12.4515 | 30.9802 | 7.2634 | 45.3925 | 5.606 | 56.2804 | 6.1217 | 67.8532 | 7.4622 | 81.4791 | 8.7482 | 103.8914 | 10.0427 | 141.0826 | 7.8134 | 190.061 | 6.4808 | 216.6634 | 8.1731 | 261.2152 | 10.2251 | 322.2554 | 11.5866 | 477.3948 | 49.6922 | 776.1482 | 42.8132
15.6951 | 11.1545 | 21.335 | 11.1434 | 32.6664 | 6.283 | 47.1978 | 5.0472 | 58.8709 | 5.4512 | 70.5517 | 6.6715 | 83.7927 | 7.8605 | 108.1312 | 8.7657 | 146.4005 | 6.8335 | 198.0154 | 5.6794 | 223.0386 | 7.2199 | 269.9791 | 9.0598 | 330.744 | 10.4525 | 488.991 | 44.427 | 790.2452 | 39.1675
16.1893 | 10.0427 | 21.897 | 10.0729 | 34.3413 | 5.495 | 49.4196 | 4.432 | 62.0752 | 4.7296 | 73.7253 | 5.923 | 85.9139 | 7.1983 | 112.3193 | 7.7667 | 152.3751 | 6.0185 | 206.0966 | 5.0171 | 228.6848 | 6.5263 | 280.1555 | 8.0756 | 340.4759 | 9.3264 | 500.368 | 39.7197 | 804.5986 | 35.3694
16.7157 | 9.0417 | 22.4064 | 9.2891 | 36.3556 | 4.7676 | 52.0574 | 3.8839 | 65.7163 | 4.0953 | 76.8877 | 5.2532 | 89.0632 | 6.4743 | 116.7863 | 6.8953 | 159.0702 | 5.3273 | 216.0144 | 4.4231 | 234.7086 | 5.9171 | 289.2654 | 7.2561 | 348.7462 | 8.5236 | 510.4761 | 35.8322 | 822.4958 | 31.5586
17.3111 | 8.1404 | 23.0657 | 8.4811 | 38.0289 | 4.2582 | 55.1108 | 3.3597 | 69.2239 | 3.6033 | 80.5072 | 4.6545 | 92.0513 | 5.8817 | 121.674 | 6.1217 | 166.8917 | 4.6592 | 227.0896 | 3.8645 | 242.0985 | 5.3594 | 300.1687 | 6.4938 | 360.4467 | 7.6281 | 519.2285 | 32.3252 | 838.2726 | 28.4984
17.8383 | 7.3511 | 24.2241 | 7.3511 | 40.1389 | 3.7204 | 58.2268 | 2.9295 | 73.7991 | 3.0921 | 84.8891 | 4.0871 | 96.192 | 5.201 | 126.008 | 5.5171 | 174.3989 | 4.1282 | 240.6503 | 3.3262 | 251.9787 | 4.7771 | 313.3575 | 5.748 | 374.4073 | 6.8063 | 528.6591 | 28.9002 | 854.3519 | 25.3264
18.4368 | 6.6915 | 25.5171 | 6.3843 | 42.9633 | 3.1357 | 61.519 | 2.5776 | 77.2731 | 2.7755 | 89.5096 | 3.5603 | 100.1177 | 4.6267 | 131.2817 | 4.9325 | 182.7913 | 3.6614 | 256.8121 | 2.8458 | 262.5246 | 4.2881 | 326.1458 | 5.1287 | 390.077 | 6.0185 | 542.0421 | 25.3771 | 871.611 | 22.7337
19.0363 | 6.1095 | 27.095 | 5.4241 | 45.2565 | 2.7755 | 64.9324 | 2.2611 | 81.235 | 2.4715 | 94.3816 | 3.1545 | 105.1456 | 4.0871 | 136.5029 | 4.4408 | 191.9711 | 3.2409 | 272.1476 | 2.4641 | 274.608 | 3.8376 | 339.1167 | 4.6221 | 404.7802 | 5.4078 | 552.9921 | 22.5074 | 890.1085 | 20.264
19.6357 | 5.6229 | 28.7416 | 4.6499 | 47.5293 | 2.4617 | 69.0165 | 1.9716 | 85.3146 | 2.2141 | 98.5285 | 2.8543 | 110.2054 | 3.6322 | 142.6431 | 3.9663 | 204.659 | 2.7811 | 290.4248 | 2.1251 | 287.8227 | 3.4207 | 352.6036 | 4.1531 | 419.6178 | 4.8883 | 563.5994 | 20.2033 | 907.1821 | 18.299
20.4575 | 5.0725 | 30.3667 | 4.0343 | 50.1664 | 2.1768 | 74.2432 | 1.6734 | 89.6888 | 1.9854 | 103.3732 | 2.5519 | 115.0475 | 3.2669 | 149.5074 | 3.5213 | 215.7985 | 2.4691 | 306.8455 | 1.8754 | 301.0706 | 3.089 | 369.5715 | 3.6908 | 438.4931 | 4.3529 | 576.7125 | 17.6167 | 929.218 | 16.1165
21.4634 | 4.517 | 31.8917 | 3.5461 | 53.4821 | 1.8848 | 79.4673 | 1.4446 | 95.6166 | 1.7278 | 108.0232 | 2.3021 | 120.5839 | 2.9178 | 155.6089 | 3.1767 | 227.3169 | 2.1877 | 323.8707 | 1.66 | 314.2989 | 2.7978 | 387.7436 | 3.2931 | 458.6759 | 3.8684 | 587.1872 | 15.6715 | 954.6486 | 14.0672
22.609 | 3.9822 | 33.7961 | 3.0613 | 57.3599 | 1.6158 | 84.8043 | 1.2571 | 100.5189 | 1.5525 | 113.5617 | 2.0541 | 126.6396 | 2.5931 | 162.2836 | 2.8859 | 239.2107 | 1.952 | 340.8166 | 1.4871 | 331.7377 | 2.4864 | 406.4025 | 2.9442 | 481.2294 | 3.4207 | 599.6486 | 13.7199 | 980.7751 | 12.4018
23.792 | 3.5108 | 35.7785 | 2.664 | 61.4575 | 1.3991 | 93.817 | 1.0139 | 107.4844 | 1.3564 | 118.9074 | 1.8531 | 133.9338 | 2.2792 | 169.7532 | 2.5853 | 254.0027 | 1.7089 | 356.5036 | 1.3551 | 347.0068 | 2.2521 | 424.6834 | 2.6375 | 503.883 | 3.0613 | 610.5399 | 12.0473 | 1011.655 | 10.7709
25.0118 | 3.1076 | 37.7636 | 2.323 | 66.1779 | 1.1946 | 106.4149 | 0.77945 | 114.7029 | 1.1804 | 125.8821 | 1.6386 | 140.66 | 2.0459 | 178.6351 | 2.2884 | 272.6925 | 1.4694 | 383.5018 | 1.1675 | 365.5286 | 2.0195 | 446.9041 | 2.3323 | 528.1308 | 2.7315 | 621.6291 | 10.5787 | 1040.382 | 9.5529
26.1369 | 2.7894 | 40.1389 | 2.0235 | 72.049 | 1.0028 | 122.6513 | 0.58675 | 124.8791 | 0.99088 | 132.3362 | 1.4621 | 147.8717 | 1.8401 | 187.2314 | 2.0644 | 293.3436 | 1.2622 | 418.3608 | 0.97418 | 386.1957 | 1.8146 | 475.9649 | 2.0276 | 551.3356 | 2.4691 | 631.6552 | 9.4389 | 1076.363 | 8.3632
27.5044 | 2.4617 | 42.4933 | 1.7592 | 77.1187 | 0.86057 | 139.3997 | 0.45377 | 135.6863 | 0.83097 | 141.0826 | 1.2774 | 156.5453 | 1.6304 | 198.2136 | 1.8182 | 313.3575 | 1.0951 | 449.5937 | 0.83765 | 408.0314 | 1.6255 | 505.9025 | 1.768 | 575.5601 | 2.2319 | 643.7714 | 8.3632 | 1120.29 | 7.1409
28.6842 | 2.2274 | 45.3471 | 1.5096 | 82.2979 | 0.75114 | 153.4455 | 0.37375 | 146.9872 | 0.71094 | 149.9565 | 1.1195 | 165.7276 | 1.4577 | 208.5847 | 1.6207 | 339.1167 | 0.93505 | 487.5262 | 0.71023 | 433.6961 | 1.4403 | 534.5065 | 1.5634 | 601.4503 | 2.0134 | 657.4335 | 7.4249 | 1164.844 | 6.1217
30.1851 | 1.9716 | 48.2476 | 1.3084 | 89.9583 | 0.62365 | 174.9229 | 0.28876 | 156.0763 | 0.62553 | 160.0275 | 0.97613 | 174.9229 | 1.3098 | 219.718 | 1.4461 | 372.5399 | 0.77324 | 546.9426 | 0.5643 | 460.5144 | 1.2774 | 569.8332 | 1.3591 | 627.8766 | 1.8346 | 672.7297 | 6.6582 | 1205.13 | 5.3755
31.828 | 1.7347 | 51.2824 | 1.1364 | 97.6457 | 0.52826 | 194.2887 | 0.23383 | 164.901 | 0.55757 | 177.389 | 0.79044 | 186.1114 | 1.1559 | 235.8851 | 1.2446 | 408.8483 | 0.64136 | 606.8876 | 0.45787 | 490.4602 | 1.1262 | 610.5399 | 1.1827 | 664.0408 | 1.6272 | 684.9484 | 6.0366 | 1250.555 | 4.6825
33.4934 | 1.5432 | 54.5625 | 0.98791 | 106.3086 | 0.44345 | 216.2305 | 0.18878 | 173.7027 | 0.49899 | 192.5479 | 0.66754 | 197.4223 | 1.0282 | 253.4951 | 1.0649 | 441.132 | 0.54653 | 670.0442 | 0.37413 | 527.0756 | 0.97515 | 652.1951 | 1.0252 | 706.5144 | 1.416 | 702.288 | 5.397 | 1302.894 | 4.0465
35.3517 | 1.3687 | 58.2851 | 0.85286 | 117.96 | 0.36054 | 238.2558 | 0.15503 | 185.3684 | 0.43729 | 212.3732 | 0.54763 | 209.0022 | 0.91745 | 271.0612 | 0.9202 | 476.9177 | 0.46712 | 764.5928 | 0.28703 | 581.9263 | 0.80561 | 691.8322 | 0.90379 | 753.2096 | 1.2384 | 721.5081 | 4.8397 | 1352.003 | 3.5532
37.4627 | 1.1982 | 62.3863 | 0.7348 | 127.2745 | 0.30908 | 265.4283 | 0.12528 | 203.4347 | 0.36234 | 233.7717 | 0.45106 | 222.8157 | 0.80803 | 293.6371 | 0.7779 | 524.9715 | 0.38707 | 839.1113 | 0.23855 | 622.2512 | 0.69966 | 755.4726 | 0.75265 | 806.2093 | 1.0745 | 742.7382 | 4.366 | 1397.364 | 3.1672
39.6205 | 1.0501 | 67.7853 | 0.61253 | 138.1508 | 0.26364 | 304.4006 | 0.09564 | 223.2617 | 0.30145 | 266.2258 | 0.34814 | 238.0176 | 0.7074 | 315.5587 | 0.67021 | 583.6747 | 0.31312 | 922.736 | 0.19747 | 661.39 | 0.61807 | 844.1611 | 0.6022 | 851.7929 | 0.95584 | 765.3578 | 3.9426 | 1452.938 | 2.7839
41.9025 | 0.91836 | 75.3652 | 0.48619 | 152.5276 | 0.21737 | 347.7015 | 0.072864 | 245.5118 | 0.24879 | 291.8805 | 0.28992 | 254.2568 | 0.62116 | 339.7957 | 0.57398 | 645.0601 | 0.25611 | 1020.801 | 0.16135 | 708.6371 | 0.53786 | 960.3935 | 0.4634 | 913.5546 | 0.83347 | 786.304 | 3.6069 | 1516.776 | 2.4202
43.8312 | 0.826 | 82.959 | 0.39965 | 169.923 | 0.17549 | 390.858 | 0.057661 | 276.537 | 0.19668 | 323.547 | 0.23642 | 281.5598 | 0.50755 | 369.5715 | 0.47704 | 733.8785 | 0.19747 | 1116.934 | 0.13504 | 769.1942 | 0.4565 | 1064.588 | 0.37375 | 973.9337 | 0.7304 | 812.6849 | 3.2702 | 1561.407 | 2.2097
46.9624 | 0.71023 | 90.4997 | 0.33348 | 188.1699 | 0.14339 | 440.6911 | 0.045585 | 299.2695 | 0.16811 | 362.6159 | 0.18822 | 320.3277 | 0.39213 | 399.1528 | 0.40936 | 828.2734 | 0.15487 | 1235.638 | 0.11045 | 845.851 | 0.37864 | 1184.816 | 0.30296 | 1043.508 | 0.63562 | 840.7913 | 2.959 | 1621.882 | 1.9637
49.3702 | 0.63245 | 100.5189 | 0.26736 | 211.1027 | 0.11404 | 491.442 | 0.036693 | 338.4392 | 0.13118 | 400.7526 | 0.15425 | 364.7982 | 0.30326 | 443.7868 | 0.33382 | 914.4688 | 0.12743 | 1379.316 | 0.088729 | 915.3836 | 0.3233 | 1327.885 | 0.24143 | 1123.656 | 0.54763 | 868.1315 | 2.6908 | 1689.761 | 1.7417
52.0574 | 0.56261 | 112.2071 | 0.21392 | 236.8305 | 0.090885 | 548.0376 | 0.029565 | 379.6859 | 0.10444 | 450.4937 | 0.12183 | 414.198 | 0.23547 | 497.3749 | 0.26523 | 1013.681 | 0.1035 | 1544.326 | 0.070639 | 1011.655 | 0.26443 | 1477.849 | 0.19414 | 1207.543 | 0.47371 | 899.0542 | 2.4494 | 1779.953 | 1.5081
54.836 | 0.5035 | 122.774 | 0.17868 | 267.0257 | 0.071851 | 597.8524 | 0.024645 | 422.143 | 0.084065 | 490.4602 | 0.10237 | 467.0069 | 0.1856 | 559.1087 | 0.20947 | 1121.411 | 0.084655 | 1769.306 | 0.053871 | 1111.364 | 0.22021 | 1669.605 | 0.1518 | 1293.805 | 0.41182 | 936.6814 | 2.1899 | 1873.085 | 1.3137
57.8207 | 0.44836 | 133.7999 | 0.1512 | 302.5797 | 0.055901 | 660.7289 | 0.020097 | 467.0069 | 0.069241 | 538.7997 | 0.08474 | 517.1556 | 0.15135 | 620.3871 | 0.17031 | 1227.019 | 0.071136 | 2051.532 | 0.040068 | 1209.961 | 0.18523 | 1869.343 | 0.1211 | 1394.572 | 0.35304 | 974.9081 | 1.9677 | 1984.937 | 1.1375
61.2734 | 0.39528 | 143.5015 | 0.13171 | 341.8406 | 0.043798 | 743.4812 | 0.016 | 514.0621 | 0.057202 | 603.8608 | 0.067396 | 573.836 | 0.12219 | 700.8848 | 0.1325 | 1376.56 | 0.056294 | 2352.755 | 0.030557 | 1325.232 | 0.15379 | 2095.07 | 0.096505 | 1500.183 | 0.3057 | 1015.71 | 1.7698 | 2105.572 | 0.99187
64.415 | 0.35588 | 154.678 | 0.11348 | 378.5485 | 0.035823 | 823.3186 | 0.013073 | 566.9912 | 0.04688 | 663.3771 | 0.055567 | 646.3516 | 0.096505 | 776.9247 | 0.10848 | 1547.417 | 0.044594 | 2618.461 | 0.024769 | 1450.035 | 0.12884 | 2417.144 | 0.072428 | 1661.278 | 0.24928 | 1063.524 | 1.5854 | 2233.538 | 0.86575
67.989 | 0.31754 | 166.7249 | 0.097963 | 425.1084 | 0.028406 | 899.0542 | 0.010942 | 638.6417 | 0.037025 | 728.0309 | 0.046367 | 709.3461 | 0.080286 | 873.356 | 0.085592 | 1748.201 | 0.035078 | 2940.52 | 0.019699 | 1594.543 | 0.10665 | 2730.778 | 0.056974 | 1825.013 | 0.20553 | 1124.78 | 1.3963 | 2426.832 | 0.72313
71.977 | 0.28332 | 179.5305 | 0.084486 | 469.3477 | 0.023326 | 938.5567 | 0.01 | 703.6938 | 0.030374 | 823.3186 | 0.036147 | 805.4035 | 0.06209 | 963.279 | 0.070639 | 1967.152 | 0.02776 | 3269.334 | 0.016 | 1803.244 | 0.083395 | 3005.928 | 0.046974 | 2031.119 | 0.16693 | 1218.46 | 1.164 | 2714.443 | 0.5643
75.6673 | 0.25534 | 196.0452 | 0.071207 | 525.4966 | 0.018645 |  |  | 794.2065 | 0.023917 | 911.7294 | 0.029359 | 896.361 | 0.05038 | 1062.461 | 0.05795 | 2242.49 | 0.021426 | 3595.152 | 0.013258 | 2065.943 | 0.063662 | 3308.803 | 0.038768 | 2217.958 | 0.13985 | 1327.885 | 0.96545 | 3036.138 | 0.44523
80.1056 | 0.22737 | 211.9489 | 0.060922 | 581.3446 | 0.015327 |  |  | 876.8564 | 0.019621 | 1018.762 | 0.023537 | 1021.823 | 0.038845 | 1186.002 | 0.046739 | 2528.4 | 0.01682 | 3949.489 | 0.011063 | 2343.362 | 0.049333 | 3656.792 | 0.031772 | 2446.325 | 0.11485 | 1435.606 | 0.81289 | 3362.169 | 0.35802
85.2294 | 0.20106 | 231.6772 | 0.050886 | 622.2512 | 0.013364 |  |  | 978.8154 | 0.015715 | 1136.085 | 0.01887 | 1145.21 | 0.030926 | 1333.207 | 0.036988 | 2830.877 | 0.013364 | 4156.137 | 0.01 | 2595 | 0.040229 | 4110.67 | 0.025219 | 2692.814 | 0.094973 | 1552.067 | 0.68855 | 3738.133 | 0.28646
91.0443 | 0.17619 | 253.4951 | 0.042631 | 675.426 | 0.011366 |  |  | 1064.588 | 0.013258 | 1266.918 | 0.015235 | 1278.372 | 0.024918 | 1498.684 | 0.029329 | 3103.674 | 0.011096 |  |  | 2911.262 | 0.031899 | 4667.325 | 0.019542 | 2958.217 | 0.078539 | 1718.733 | 0.55203 | 4110.67 | 0.23383
96.9646 | 0.15534 | 278.4795 | 0.035396 | 720.0664 | 0.01 |  |  | 1159.035 | 0.011208 | 1379.316 | 0.012918 | 1393.178 | 0.020959 | 1659.618 | 0.023917 | 3269.334 | 0.01 |  |  | 3220.66 | 0.026117 | 5127.334 | 0.016242 | 3217.441 | 0.066526 | 1837.833 | 0.47943 | 4430.826 | 0.20126
105.567 | 0.13131 | 302.5797 | 0.030072 |  |  |  |  | 1228.247 | 0.01 | 1485.256 | 0.01114 | 1552.067 | 0.016888 | 1837.833 | 0.019406 |  |  |  |  | 3613.173 | 0.02073 | 5621.428 | 0.013458 | 3548.718 | 0.05474 | 1961.26 | 0.41805 | 4823.916 | 0.16912
112.8823 | 0.11508 | 334.7367 | 0.024547 | [6 empty] | 1566.098 | 0.01 | 1748.201 | 0.013298 | 2039.26 | 0.01573 |  |  |  |  | 3989.182 | 0.017074 | 6138.532 | 0.01132 | 3949.489 | 0.044327 | 2095.07 | 0.3638 | 5325.922 | 0.13832
124.2562 | 0.094878 | 368.4645 | 0.02032 | [8 empty] | 1924.348 | 0.010997 | 2240.249 | 0.013047 |  |  |  |  | 4435.259 | 0.01373 | 6518.117 | 0.01 | 4453.036 | 0.034869 | 2274.105 | 0.30784 | 5850.843 | 0.1145
133.9338 | 0.081907 | 406.4025 | 0.016787 | [8 empty] | 2004.886 | 0.01 | 2424.407 | 0.011174 |  |  |  |  | 4946.033 | 0.011107 |  |  | 4946.033 | 0.028264 | 2488.268 | 0.25611 | 6440.368 | 0.094688
151.6152 | 0.064109 | 455.9322 | 0.013351 | [10 empty] | 2558.924 | 0.01 |  |  |  |  | 5210.031 | 0.01 |  |  | 5526.672 | 0.022682 | 2695.508 | 0.21759 | 6962.827 | 0.081011
166.7249 | 0.053175 | 500.368 | 0.011074 | [20 empty] | 6126.268 | 0.018497 | 2943.462 | 0.18265 | 7588.132 | 0.068278
189.4917 | 0.041206 | 526.5488 | 0.01 | [20 empty] | 6770.572 | 0.015159 | 3188.614 | 0.15565 | 8187.31 | 0.058709
214.5075 | 0.03222 | [22 empty] | 7408.185 | 0.012725 | 3433.521 | 0.13423 | 8886.962 | 0.049829
237.3046 | 0.02638 | [22 empty] | 8001.15 | 0.01092 | 3726.936 | 0.11416 | 9550.42 | 0.043232
264.3687 | 0.021255 | [22 empty] | 8361.061 | 0.01 | 4098.357 | 0.094783 | 10000 | 0.039551
290.1345 | 0.017647 | [24 empty] | 4524.857 | 0.077679
325.1688 | 0.014092 | [24 empty] | 5010.751 | 0.063662
362.6159 | 0.011331 | [24 empty] | 5477.155 | 0.053175
385.8097 | 0.01 | [24 empty] | 5998.958 | 0.044282
[26 empty] | 6427.5 | 0.038497
[26 empty] | 6941.97 | 0.032937
[26 empty] | 7482.638 | 0.028292
[26 empty] | 8130.199 | 0.024013
[26 empty] | 8719.704 | 0.020813
[26 empty] | 9380.051 | 0.01795
[26 empty] | 10000 | 0.015667