## S&C "K" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "K" Speed | [11 empty] | S&C "K" Speed | [11 empty] | S&C "K" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023
Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance:
2K |  |  |  | 3K |  |  |  | 5K |  |  |  | 6K |  |  |  | 8K |  |  |  | 10K |  |  |  | 12K |  |  |  | 15K |  |  |  | 20K
Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s
5 | 4.1135 | 5 | 9.6503 | 7 | 8.0114 | 7 | 20.9312 | 11 | 8.2025 | 11 | 25.7642 | 13 | 18.9683 | 13 | 216.7189 | 16 | 15.418 | 16 | 344.0888 | 21 | 20.1987 | 21 | 444.4323 | 29 | 14.2179 | 29 | 89.7781 | 34 | 24.2206 | 34 | 784.0237 | 44 | 23.3215 | 44 | 999.7056
6 | 2.4522 | 6 | 4.1255 | 8 | 4.7145 | 8 | 8.0234 | 12 | 4.7121 | 12 | 8.2145 | 14 | 9.5796 | 14 | 18.9803 | 17 | 10.1452 | 17 | 30.341 | 22 | 13.3783 | 22 | 39.4721 | 30 | 10.9459 | 30 | 33.0979 | 35 | 18.0584 | 35 | 70.2513 | 45 | 15.3412 | 45 | 89.8709
7 | 1.6728 | 7 | 2.4642 | 9 | 3.2293 | 9 | 4.7265 | 13 | 3.2284 | 13 | 4.7241 | 15 | 6.2649 | 15 | 9.5916 | 18 | 7.4571 | 18 | 15.43 | 23 | 9.8949 | 23 | 20.2107 | 31 | 8.8471 | 31 | 20.0298 | 36 | 11.8091 | 36 | 36.2777 | 46 | 13.0416 | 46 | 46.5574
8 | 1.2297 | 8 | 1.6848 | 10 | 2.3952 | 10 | 3.2413 | 14 | 2.4125 | 14 | 3.2404 | 16 | 3.5616 | 16 | 6.2769 | 19 | 5.8324 | 19 | 10.1572 | 24 | 7.7851 | 24 | 13.3903 | 32 | 7.3883 | 32 | 14.2299 | 37 | 10.0104 | 37 | 24.2326 | 47 | 11.3123 | 47 | 31.1959
9 | 0.94888 | 9 | 1.2417 | 11 | 1.8671 | 11 | 2.4072 | 15 | 1.8994 | 15 | 2.4245 | 17 | 2.8844 | 17 | 4.5904 | 20 | 4.7476 | 20 | 7.4691 | 25 | 5.3634 | 25 | 9.9069 | 33 | 6.3165 | 33 | 10.9579 | 38 | 8.659 | 38 | 18.0704 | 48 | 9.9653 | 48 | 23.3335
10 | 0.75763 | 10 | 0.96088 | 12 | 1.5061 | 12 | 1.8791 | 16 | 1.2951 | 16 | 1.9114 | 18 | 2.4028 | 18 | 3.5736 | 21 | 3.9741 | 21 | 5.8444 | 26 | 4.607 | 26 | 7.7971 | 34 | 5.4967 | 34 | 8.8591 | 39 | 7.6072 | 39 | 14.3304 | 49 | 8.8869 | 49 | 18.5588
11 | 0.62063 | 11 | 0.76963 | 13 | 1.246 | 13 | 1.5181 | 17 | 1.104 | 17 | 1.5607 | 19 | 2.044 | 19 | 2.8964 | 22 | 3.3962 | 22 | 4.7596 | 27 | 4.0202 | 27 | 6.385 | 35 | 4.8499 | 35 | 7.4003 | 40 | 6.766 | 40 | 11.8211 | 50 | 8.0045 | 50 | 15.3532
12 | 0.51868 | 12 | 0.63263 | 14 | 1.051 | 14 | 1.258 | 18 | 0.95543 | 18 | 1.3071 | 20 | 1.7673 | 20 | 2.4148 | 23 | 2.949 | 23 | 3.9861 | 28 | 3.5524 | 28 | 5.3754 | 36 | 3.8964 | 36 | 6.3285 | 41 | 6.0784 | 41 | 10.0224 | 51 | 7.2695 | 51 | 13.0536
13 | 0.44052 | 13 | 0.53068 | 15 | 0.90036 | 15 | 1.063 | 19 | 0.83699 | 19 | 1.116 | 21 | 1.5479 | 21 | 2.056 | 24 | 2.5936 | 24 | 3.4082 | 29 | 3.1712 | 29 | 4.619 | 37 | 3.5355 | 37 | 5.5087 | 42 | 5.5063 | 42 | 8.671 | 52 | 6.648 | 52 | 11.3243
14 | 0.37916 | 14 | 0.45252 | 16 | 0.68502 | 16 | 0.91236 | 20 | 0.7407 | 20 | 0.96743 | 22 | 1.3703 | 22 | 1.7793 | 25 | 2.0663 | 25 | 2.961 | 30 | 2.8552 | 30 | 4.0322 | 38 | 3.229 | 38 | 4.8619 | 43 | 5.0231 | 43 | 7.6192 | 53 | 6.1159 | 53 | 9.9773
15 | 0.33002 | 15 | 0.39116 | 17 | 0.60614 | 17 | 0.79319 | 21 | 0.6611 | 21 | 0.84899 | 23 | 1.2239 | 23 | 1.5599 | 26 | 1.8661 | 26 | 2.6056 | 31 | 2.5892 | 31 | 3.5644 | 39 | 2.9657 | 39 | 4.3392 | 44 | 4.6099 | 44 | 6.778 | 54 | 5.6554 | 54 | 8.8989
16 | 0.25697 | 16 | 0.34202 | 18 | 0.54053 | 18 | 0.69702 | 22 | 0.59439 | 22 | 0.7527 | 24 | 1.1014 | 24 | 1.3823 | 27 | 1.696 | 27 | 2.317 | 32 | 2.3625 | 32 | 3.1832 | 40 | 2.7372 | 40 | 3.9084 | 45 | 3.941 | 45 | 6.0904 | 55 | 4.8987 | 55 | 8.0165
17 | 0.22934 | 17 | 0.30201 | 19 | 0.48531 | 19 | 0.61814 | 23 | 0.53781 | 23 | 0.6731 | 25 | 0.90881 | 25 | 1.2359 | 28 | 1.5499 | 28 | 2.0783 | 33 | 2.1673 | 33 | 2.8672 | 41 | 2.5373 | 41 | 3.5475 | 46 | 3.6668 | 46 | 5.5183 | 56 | 4.5844 | 56 | 7.2815
18 | 0.206 | 18 | 0.26897 | 20 | 0.43834 | 20 | 0.55253 | 24 | 0.48933 | 24 | 0.60639 | 26 | 0.83202 | 26 | 1.1134 | 29 | 1.4233 | 29 | 1.8781 | 34 | 1.9976 | 34 | 2.6012 | 42 | 2.361 | 42 | 3.241 | 47 | 3.4239 | 47 | 5.0351 | 57 | 4.3037 | 57 | 6.66
19 | 0.18609 | 19 | 0.24134 | 21 | 0.39803 | 21 | 0.49731 | 25 | 0.41089 | 25 | 0.54981 | 27 | 0.7651 | 27 | 1.0097 | 30 | 1.3126 | 30 | 1.708 | 35 | 1.8488 | 35 | 2.3745 | 43 | 2.2044 | 43 | 2.9777 | 48 | 3.2073 | 48 | 4.6219 | 58 | 4.0517 | 58 | 6.1279
20 | 0.16896 | 20 | 0.218 | 22 | 0.36314 | 22 | 0.45034 | 26 | 0.37884 | 26 | 0.50133 | 28 | 0.70637 | 28 | 0.92081 | 31 | 1.2152 | 31 | 1.5619 | 36 | 1.6009 | 36 | 2.1793 | 44 | 2.0646 | 44 | 2.7492 | 49 | 3.0131 | 49 | 4.2647 | 59 | 3.8242 | 59 | 5.6674
21 | 0.15412 | 21 | 0.19809 | 23 | 0.33274 | 23 | 0.41003 | 27 | 0.35054 | 27 | 0.45941 | 29 | 0.65447 | 29 | 0.84402 | 32 | 1.129 | 32 | 1.4353 | 37 | 1.4967 | 37 | 2.0096 | 45 | 1.8256 | 45 | 2.5493 | 50 | 2.838 | 50 | 3.953 | 60 | 3.618 | 60 | 5.2651
22 | 0.14116 | 22 | 0.18096 | 24 | 0.30607 | 24 | 0.37514 | 28 | 0.3254 | 28 | 0.42289 | 30 | 0.60836 | 30 | 0.7771 | 33 | 1.0522 | 33 | 1.3246 | 38 | 1.4031 | 38 | 1.8608 | 46 | 1.7228 | 46 | 2.373 | 51 | 2.6794 | 51 | 3.6788 | 61 | 3.4301 | 61 | 4.9107
23 | 0.12979 | 23 | 0.16612 | 25 | 0.26166 | 25 | 0.34474 | 29 | 0.30297 | 29 | 0.39084 | 31 | 0.56718 | 31 | 0.71837 | 34 | 0.98335 | 34 | 1.2272 | 39 | 1.3186 | 39 | 1.7295 | 47 | 1.6293 | 47 | 2.2164 | 52 | 2.5352 | 52 | 3.4359 | 62 | 3.2584 | 62 | 4.5964
24 | 0.11975 | 24 | 0.15316 | 26 | 0.24305 | 26 | 0.31807 | 30 | 0.28285 | 30 | 0.36254 | 32 | 0.53021 | 32 | 0.66647 | 35 | 0.92144 | 35 | 1.141 | 40 | 1.2421 | 40 | 1.6129 | 48 | 1.5439 | 48 | 2.0766 | 53 | 2.4036 | 53 | 3.2193 | 63 | 3.1009 | 63 | 4.3157
25 | 0.10289 | 25 | 0.14179 | 27 | 0.22638 | 27 | 0.29454 | 31 | 0.26472 | 31 | 0.3374 | 33 | 0.49688 | 33 | 0.62036 | 36 | 0.81474 | 36 | 1.0642 | 41 | 1.1725 | 41 | 1.5087 | 49 | 1.4656 | 49 | 1.9509 | 54 | 2.283 | 54 | 3.0251 | 64 | 2.9559 | 64 | 4.0637
26 | 0.09578 | 26 | 0.13175 | 28 | 0.21139 | 28 | 0.27366 | 32 | 0.24834 | 32 | 0.31497 | 34 | 0.46672 | 34 | 0.57918 | 37 | 0.76853 | 37 | 0.99535 | 42 | 1.1089 | 42 | 1.4151 | 50 | 1.3936 | 50 | 1.8376 | 55 | 2.0699 | 55 | 2.85 | 65 | 2.6982 | 65 | 3.8362
27 | 0.08938 | 27 | 0.12284 | 29 | 0.19786 | 29 | 0.25505 | 33 | 0.23347 | 33 | 0.29485 | 35 | 0.43932 | 35 | 0.54221 | 38 | 0.72632 | 38 | 0.93344 | 43 | 1.0508 | 43 | 1.3306 | 51 | 1.3272 | 51 | 1.7349 | 56 | 1.9755 | 56 | 2.6914 | 66 | 2.5831 | 66 | 3.63
28 | 0.0836 | 28 | 0.11489 | 30 | 0.18561 | 30 | 0.23838 | 34 | 0.21993 | 34 | 0.27672 | 36 | 0.39151 | 36 | 0.50888 | 39 | 0.68764 | 39 | 0.87749 | 44 | 0.99729 | 44 | 1.2541 | 52 | 1.2658 | 52 | 1.6413 | 57 | 1.8879 | 57 | 2.5472 | 67 | 2.4761 | 67 | 3.4421
29 | 0.07837 | 29 | 0.10778 | 31 | 0.17447 | 31 | 0.22339 | 35 | 0.20756 | 35 | 0.26034 | 37 | 0.37058 | 37 | 0.47872 | 40 | 0.6521 | 40 | 0.82674 | 45 | 0.90254 | 45 | 1.1845 | 53 | 1.2088 | 53 | 1.5559 | 58 | 1.8065 | 58 | 2.4156 | 68 | 2.3764 | 68 | 3.2704
30 | 0.07362 | 30 | 0.10138 | 32 | 0.16431 | 32 | 0.20986 | 36 | 0.18583 | 36 | 0.24547 | 38 | 0.35132 | 38 | 0.45132 | 41 | 0.61935 | 41 | 0.78053 | 46 | 0.86042 | 46 | 1.1209 | 54 | 1.156 | 54 | 1.4776 | 59 | 1.7308 | 59 | 2.295 | 69 | 2.2831 | 69 | 3.1129
31 | 0.06929 | 31 | 0.0956 | 33 | 0.15502 | 33 | 0.19761 | 37 | 0.17624 | 37 | 0.23193 | 39 | 0.33358 | 39 | 0.42635 | 42 | 0.5891 | 42 | 0.73832 | 47 | 0.82133 | 47 | 1.0628 | 55 | 1.0608 | 55 | 1.4056 | 60 | 1.6601 | 60 | 2.1841 | 70 | 2.1958 | 70 | 2.9679
32 | 0.06534 | 32 | 0.09037 | 34 | 0.14651 | 34 | 0.18647 | 38 | 0.1674 | 38 | 0.21956 | 40 | 0.31718 | 40 | 0.40351 | 43 | 0.56109 | 43 | 0.69964 | 48 | 0.78498 | 48 | 1.0093 | 56 | 1.0178 | 56 | 1.3392 | 61 | 1.5939 | 61 | 2.0819 | 71 | 2.114 | 71 | 2.8341
33 | 0.06171 | 33 | 0.08562 | 35 | 0.13869 | 35 | 0.17631 | 39 | 0.15922 | 39 | 0.20823 | 41 | 0.30199 | 41 | 0.38258 | 44 | 0.53511 | 44 | 0.6641 | 49 | 0.7511 | 49 | 0.96004 | 57 | 0.97758 | 57 | 1.2778 | 62 | 1.532 | 62 | 1.9875 | 72 | 2.037 | 72 | 2.7102
34 | 0.05838 | 34 | 0.08129 | 36 | 0.12482 | 36 | 0.16702 | 40 | 0.15163 | 40 | 0.19783 | 42 | 0.28789 | 42 | 0.36332 | 45 | 0.48843 | 45 | 0.63135 | 50 | 0.71947 | 50 | 0.91454 | 58 | 0.93984 | 58 | 1.2208 | 63 | 1.4739 | 63 | 1.8999 | 73 | 1.9646 | 73 | 2.5951
35 | 0.05531 | 35 | 0.07734 | 37 | 0.11866 | 37 | 0.15851 | 41 | 0.14458 | 41 | 0.18824 | 43 | 0.27478 | 43 | 0.34558 | 46 | 0.46743 | 46 | 0.6011 | 51 | 0.68988 | 51 | 0.87242 | 59 | 0.90437 | 59 | 1.168 | 64 | 1.4193 | 64 | 1.8185 | 74 | 1.8963 | 74 | 2.4881
36 | 0.04986 | 36 | 0.07371 | 38 | 0.11295 | 38 | 0.15069 | 42 | 0.13802 | 42 | 0.1794 | 44 | 0.26257 | 44 | 0.32918 | 47 | 0.44778 | 47 | 0.57309 | 52 | 0.66216 | 52 | 0.83333 | 60 | 0.87099 | 60 | 1.1187 | 65 | 1.3194 | 65 | 1.7428 | 75 | 1.8319 | 75 | 2.3884
37 | 0.04743 | 37 | 0.07038 | 39 | 0.10764 | 39 | 0.14348 | 43 | 0.13191 | 43 | 0.17122 | 45 | 0.24052 | 45 | 0.31399 | 48 | 0.42939 | 48 | 0.54711 | 53 | 0.63615 | 53 | 0.79698 | 61 | 0.83954 | 61 | 1.0728 | 66 | 1.2736 | 66 | 1.6721 | 76 | 1.7133 | 76 | 2.2951
38 | 0.04518 | 38 | 0.06731 | 40 | 0.1027 | 40 | 0.13682 | 44 | 0.12619 | 44 | 0.16363 | 46 | 0.23054 | 46 | 0.29989 | 49 | 0.41214 | 49 | 0.52294 | 54 | 0.6117 | 54 | 0.7631 | 62 | 0.80985 | 62 | 1.0298 | 67 | 1.2303 | 67 | 1.6059 | 77 | 1.6587 | 77 | 2.2078
39 | 0.04308 | 39 | 0.06448 | 41 | 0.0981 | 41 | 0.13066 | 45 | 0.11584 | 45 | 0.15658 | 47 | 0.22118 | 47 | 0.28678 | 50 | 0.39593 | 50 | 0.50043 | 55 | 0.567 | 55 | 0.73147 | 63 | 0.78179 | 63 | 0.98958 | 68 | 1.1894 | 68 | 1.544 | 78 | 1.6068 | 78 | 2.126
40 | 0.04113 | 40 | 0.06186 | 42 | 0.0938 | 42 | 0.12495 | 46 | 0.11115 | 46 | 0.15002 | 48 | 0.21239 | 48 | 0.27457 | 51 | 0.38069 | 51 | 0.47943 | 56 | 0.54653 | 56 | 0.70188 | 64 | 0.75524 | 64 | 0.95184 | 69 | 1.1506 | 69 | 1.4859 | 79 | 1.5575 | 79 | 2.049
41 | 0.03931 | 41 | 0.05943 | 43 | 0.08978 | 43 | 0.11964 | 47 | 0.10673 | 47 | 0.14391 | 49 | 0.20413 | 49 | 0.26317 | 52 | 0.36633 | 52 | 0.45978 | 57 | 0.52719 | 57 | 0.67416 | 65 | 0.70624 | 65 | 0.91637 | 70 | 1.1137 | 70 | 1.4313 | 80 | 1.5107 | 80 | 1.9766
42 | 0.0376 | 42 | 0.05718 | 44 | 0.08601 | 44 | 0.1147 | 48 | 0.10258 | 48 | 0.13819 | 50 | 0.19635 | 50 | 0.25252 | 53 | 0.35279 | 53 | 0.44139 | 58 | 0.50889 | 58 | 0.64815 | 66 | 0.6836 | 66 | 0.88299 | 71 | 1.0788 | 71 | 1.3799 | 81 | 1.4661 | 81 | 1.9083
43 | 0.03601 | 43 | 0.05508 | 45 | 0.07916 | 45 | 0.1101 | 49 | 0.09867 | 49 | 0.13285 | 51 | 0.18901 | 51 | 0.24254 | 54 | 0.34001 | 54 | 0.42414 | 59 | 0.49156 | 59 | 0.6237 | 67 | 0.66208 | 67 | 0.85154 | 72 | 1.0455 | 72 | 1.3314 | 82 | 1.4236 | 82 | 1.8439
44 | 0.03451 | 44 | 0.05313 | 46 | 0.07604 | 46 | 0.1058 | 50 | 0.09498 | 50 | 0.12784 | 52 | 0.18208 | 52 | 0.23318 | 55 | 0.31648 | 55 | 0.40793 | 60 | 0.47513 | 60 | 0.60068 | 68 | 0.64161 | 68 | 0.82185 | 73 | 1.0138 | 73 | 1.2856 | 83 | 1.383 | 83 | 1.783
45 | 0.015625 | 45 | 0.05131 | 47 | 0.0731 | 47 | 0.10178 | 51 | 0.09149 | 51 | 0.12315 | 53 | 0.17553 | 53 | 0.22439 | 56 | 0.30564 | 56 | 0.39269 | 61 | 0.45953 | 61 | 0.579 | 69 | 0.62211 | 69 | 0.79379 | 74 | 0.98367 | 74 | 1.2423 | 84 | 1.3443 | 84 | 1.7253
46 | 0.015625 | 46 | 0.0496 | 48 | 0.07033 | 48 | 0.09801 | 52 | 0.0882 | 52 | 0.11873 | 54 | 0.16933 | 54 | 0.21613 | 57 | 0.29536 | 57 | 0.37833 | 62 | 0.44472 | 62 | 0.55853 | 70 | 0.60353 | 70 | 0.76724 | 75 | 0.95491 | 75 | 1.2014 | 85 | 1.2719 | 85 | 1.6707
47 | 0.015625 | 47 | 0.04801 | 49 | 0.06771 | 49 | 0.09448 | 53 | 0.08508 | 53 | 0.11458 | 55 | 0.1579 | 55 | 0.20835 | 58 | 0.2856 | 58 | 0.36479 | 63 | 0.43063 | 63 | 0.53919 | 71 | 0.5858 | 71 | 0.7421 | 76 | 0.90124 | 76 | 1.1626 | 86 | 1.238 | 86 | 1.6188
48 | 0.015625 | 48 | 0.04651 | 50 | 0.06524 | 50 | 0.09116 | 54 | 0.08213 | 54 | 0.11067 | 56 | 0.15262 | 56 | 0.20101 | 59 | 0.27632 | 59 | 0.35201 | 64 | 0.41722 | 64 | 0.52089 | 72 | 0.56888 | 72 | 0.71824 | 77 | 0.87617 | 77 | 1.1257 | 87 | 1.2056 | 87 | 1.5695
49 | 0.015625 | 49 | 0.04511 | 51 | 0.0629 | 51 | 0.08804 | 55 | 0.07667 | 55 | 0.10698 | 57 | 0.1476 | 57 | 0.19408 | 60 | 0.2675 | 60 | 0.33992 | 65 | 0.39226 | 65 | 0.50356 | 73 | 0.55271 | 73 | 0.6956 | 78 | 0.85219 | 78 | 1.0908 | 88 | 1.1745 | 88 | 1.5227
50 | 0.015625 | 50 | 0.03334 | 52 | 0.06069 | 52 | 0.0851 | 56 | 0.07414 | 56 | 0.10349 | 58 | 0.14283 | 58 | 0.18753 | 61 | 0.2591 | 61 | 0.32848 | 66 | 0.38063 | 66 | 0.48713 | 74 | 0.53725 | 74 | 0.67408 | 79 | 0.82922 | 79 | 1.0575 | 89 | 1.1447 | 89 | 1.4781
453 | 0.015625 | 453 | 0.03334 | 53 | 0.05859 | 53 | 0.08233 | 57 | 0.07174 | 57 | 0.1002 | 59 | 0.13829 | 59 | 0.18133 | 62 | 0.2511 | 62 | 0.31764 | 67 | 0.36953 | 67 | 0.47153 | 75 | 0.52245 | 75 | 0.65361 | 80 | 0.80722 | 80 | 1.0258 | 90 | 1.116 | 90 | 1.4356
454 | 0.011042 | 454 | 0.03334 | 54 | 0.05659 | 54 | 0.07971 | 58 | 0.06946 | 58 | 0.09708 | 60 | 0.13397 | 60 | 0.17546 | 63 | 0.24347 | 63 | 0.30736 | 68 | 0.35892 | 68 | 0.45672 | 76 | 0.49469 | 76 | 0.63411 | 81 | 0.78612 | 81 | 0.99567 | 91 | 1.0885 | 91 | 1.395
455 | 0.001 | 455 | 0.03334 | 55 | 0.0529 | 55 | 0.07724 | 59 | 0.06728 | 59 | 0.09413 | 61 | 0.12985 | 61 | 0.1699 | 64 | 0.23619 | 64 | 0.2976 | 69 | 0.34876 | 69 | 0.44263 | 77 | 0.48167 | 77 | 0.61553 | 82 | 0.76588 | 82 | 0.96691 | 92 | 1.0621 | 92 | 1.3563
500 | 0.001 | 500 | 0.03334 | 56 | 0.05119 | 56 | 0.0749 | 60 | 0.0652 | 60 | 0.09133 | 62 | 0.12591 | 62 | 0.16462 | 65 | 0.22258 | 65 | 0.28832 | 70 | 0.33905 | 70 | 0.42922 | 78 | 0.46917 | 78 | 0.5978 | 83 | 0.74644 | 83 | 0.93946 | 93 | 1.0366 | 93 | 1.3193
501 | 0.001 | 501 | 0.01667 | 57 | 0.04957 | 57 | 0.07269 | 61 | 0.06322 | 61 | 0.08867 | 63 | 0.12216 | 63 | 0.1596 | 66 | 0.21623 | 66 | 0.2795 | 71 | 0.32974 | 71 | 0.41644 | 79 | 0.45716 | 79 | 0.58088 | 84 | 0.72776 | 84 | 0.91324 | 94 | 1.0122 | 94 | 1.2839
6300 | 0.001 | 6300 | 0.01667 | 58 | 0.04801 | 58 | 0.07059 | 62 | 0.06133 | 62 | 0.08614 | 64 | 0.11857 | 64 | 0.15483 | 67 | 0.21014 | 67 | 0.2711 | 72 | 0.32082 | 72 | 0.40426 | 80 | 0.44563 | 80 | 0.56471 | 85 | 0.69254 | 85 | 0.88817 | 95 | 0.96587 | 95 | 1.25
|  |  |  | 59 | 0.04653 | 59 | 0.06859 | 63 | 0.05952 | 63 | 0.08374 | 65 | 0.11186 | 65 | 0.15029 | 68 | 0.20431 | 68 | 0.2631 | 73 | 0.31227 | 73 | 0.39263 | 81 | 0.43455 | 81 | 0.54925 | 86 | 0.67592 | 86 | 0.86419 | 96 | 0.94398 | 96 | 1.2176
|  |  |  | 60 | 0.04512 | 60 | 0.0667 | 64 | 0.0578 | 64 | 0.08146 | 66 | 0.10872 | 66 | 0.14597 | 69 | 0.19873 | 69 | 0.25547 | 74 | 0.30406 | 74 | 0.38153 | 82 | 0.42388 | 82 | 0.53445 | 87 | 0.65992 | 87 | 0.84122 | 97 | 0.92286 | 97 | 1.1865
|  |  |  | 61 | 0.04377 | 61 | 0.0649 | 65 | 0.05456 | 65 | 0.07928 | 67 | 0.10571 | 67 | 0.14185 | 70 | 0.19337 | 70 | 0.24819 | 75 | 0.29618 | 75 | 0.37092 | 83 | 0.41362 | 83 | 0.52027 | 88 | 0.6445 | 88 | 0.81922 | 98 | 0.90248 | 98 | 1.1567
|  |  |  | 62 | 0.04248 | 62 | 0.06319 | 66 | 0.05305 | 66 | 0.0772 | 68 | 0.10282 | 68 | 0.13791 | 71 | 0.18823 | 71 | 0.24123 | 76 | 0.28132 | 76 | 0.36076 | 84 | 0.40373 | 84 | 0.50669 | 89 | 0.62964 | 89 | 0.79812 | 99 | 0.88281 | 99 | 1.128
|  |  |  | 63 | 0.04125 | 63 | 0.06157 | 67 | 0.05159 | 67 | 0.07522 | 69 | 0.10006 | 69 | 0.13416 | 72 | 0.18329 | 72 | 0.23458 | 77 | 0.27432 | 77 | 0.35105 | 85 | 0.38503 | 85 | 0.49367 | 90 | 0.6153 | 90 | 0.77788 | 100 | 0.8638 | 100 | 1.1005
|  |  |  | 64 | 0.04007 | 64 | 0.06001 | 68 | 0.0502 | 68 | 0.07333 | 70 | 0.0974 | 70 | 0.13057 | 73 | 0.17855 | 73 | 0.22823 | 78 | 0.26758 | 78 | 0.34174 | 86 | 0.37617 | 86 | 0.48117 | 91 | 0.60146 | 91 | 0.75844 | 101 | 0.84544 | 101 | 1.0741
|  |  |  | 65 | 0.03786 | 65 | 0.05853 | 69 | 0.04886 | 69 | 0.07152 | 71 | 0.09485 | 71 | 0.12714 | 74 | 0.174 | 74 | 0.22214 | 79 | 0.26109 | 79 | 0.33282 | 87 | 0.36763 | 87 | 0.46916 | 92 | 0.58811 | 92 | 0.73976 | 102 | 0.82768 | 102 | 1.0486
|  |  |  | 66 | 0.03682 | 66 | 0.05712 | 70 | 0.04758 | 70 | 0.0698 | 72 | 0.0924 | 72 | 0.12386 | 75 | 0.16961 | 75 | 0.21631 | 80 | 0.25483 | 80 | 0.32427 | 88 | 0.35938 | 88 | 0.45763 | 93 | 0.57521 | 93 | 0.72181 | 103 | 0.8105 | 103 | 1.0241
|  |  |  | 67 | 0.03583 | 67 | 0.05577 | 71 | 0.04634 | 71 | 0.06814 | 73 | 0.09004 | 73 | 0.12072 | 76 | 0.16134 | 76 | 0.21073 | 81 | 0.24881 | 81 | 0.31606 | 89 | 0.35141 | 89 | 0.44655 | 94 | 0.56274 | 94 | 0.70454 | 104 | 0.79388 | 104 | 1.0006
|  |  |  | 68 | 0.03487 | 68 | 0.05448 | 72 | 0.04516 | 72 | 0.06656 | 74 | 0.08777 | 74 | 0.11771 | 77 | 0.15743 | 77 | 0.20537 | 82 | 0.243 | 82 | 0.30818 | 90 | 0.34372 | 90 | 0.43588 | 95 | 0.53904 | 95 | 0.68792 | 105 | 0.76221 | 105 | 0.97787
|  |  |  | 69 | 0.03395 | 69 | 0.05325 | 73 | 0.04401 | 73 | 0.06505 | 75 | 0.08559 | 75 | 0.11482 | 78 | 0.15366 | 78 | 0.20023 | 83 | 0.23739 | 83 | 0.3006 | 91 | 0.33628 | 91 | 0.42562 | 96 | 0.52776 | 96 | 0.67192 | 106 | 0.74711 | 106 | 0.95598
|  |  |  | 70 | 0.03307 | 70 | 0.05207 | 74 | 0.04292 | 74 | 0.06359 | 76 | 0.08147 | 76 | 0.11206 | 79 | 0.15002 | 79 | 0.19529 | 84 | 0.23198 | 84 | 0.29332 | 92 | 0.32908 | 92 | 0.41573 | 97 | 0.51685 | 97 | 0.6565 | 107 | 0.73247 | 107 | 0.93486
|  |  |  | 71 | 0.015625 | 71 | 0.05094 | 75 | 0.04186 | 75 | 0.0622 | 77 | 0.07952 | 77 | 0.1094 | 80 | 0.14652 | 80 | 0.19055 | 85 | 0.2217 | 85 | 0.28632 | 93 | 0.32212 | 93 | 0.40621 | 98 | 0.50628 | 98 | 0.64164 | 108 | 0.71828 | 108 | 0.91448
|  |  |  | 72 | 0.015625 | 72 | 0.04986 | 76 | 0.03986 | 76 | 0.06086 | 78 | 0.07764 | 78 | 0.10685 | 81 | 0.14314 | 81 | 0.186 | 86 | 0.21682 | 86 | 0.27958 | 94 | 0.31539 | 94 | 0.39703 | 99 | 0.49604 | 99 | 0.6273 | 109 | 0.70452 | 109 | 0.89481
|  |  |  | 73 | 0.015625 | 73 | 0.04882 | 77 | 0.03891 | 77 | 0.05958 | 79 | 0.07582 | 79 | 0.1044 | 82 | 0.13987 | 82 | 0.18161 | 87 | 0.21211 | 87 | 0.27309 | 95 | 0.30255 | 95 | 0.38817 | 100 | 0.48612 | 100 | 0.61346 | 110 | 0.69116 | 110 | 0.8758
|  |  |  | 74 | 0.015625 | 74 | 0.04783 | 78 | 0.038 | 78 | 0.05834 | 80 | 0.07407 | 80 | 0.10204 | 83 | 0.13672 | 83 | 0.1774 | 88 | 0.20754 | 88 | 0.26683 | 96 | 0.29642 | 96 | 0.37963 | 101 | 0.47651 | 101 | 0.60011 | 111 | 0.6782 | 111 | 0.85744
|  |  |  | 75 | 0.015625 | 75 | 0.04687 | 79 | 0.03712 | 79 | 0.05716 | 81 | 0.07238 | 81 | 0.09977 | 84 | 0.13367 | 84 | 0.17334 | 89 | 0.20313 | 89 | 0.26081 | 97 | 0.29049 | 97 | 0.37138 | 102 | 0.46718 | 102 | 0.58721 | 112 | 0.66561 | 112 | 0.83968
|  |  |  | 76 | 0.015625 | 76 | 0.04595 | 80 | 0.03626 | 80 | 0.05601 | 82 | 0.07075 | 82 | 0.09759 | 85 | 0.12788 | 85 | 0.16943 | 90 | 0.19886 | 90 | 0.255 | 98 | 0.28474 | 98 | 0.36341 | 103 | 0.45814 | 103 | 0.57474 | 113 | 0.65339 | 113 | 0.8225
|  |  |  | 77 | 0.015625 | 77 | 0.04507 | 81 | 0.03544 | 81 | 0.05492 | 83 | 0.06917 | 83 | 0.09549 | 86 | 0.12512 | 86 | 0.16566 | 91 | 0.19472 | 91 | 0.24939 | 99 | 0.27916 | 99 | 0.35572 | 104 | 0.44936 | 104 | 0.56269 | 114 | 0.64151 | 114 | 0.80588
|  |  |  | 78 | 0.015625 | 78 | 0.03334 | 82 | 0.03465 | 82 | 0.05386 | 84 | 0.06764 | 84 | 0.09347 | 87 | 0.12246 | 87 | 0.16202 | 92 | 0.19071 | 92 | 0.24398 | 100 | 0.27375 | 100 | 0.34828 | 105 | 0.43256 | 105 | 0.55104 | 115 | 0.61875 | 115 | 0.78979
|  |  |  | 453 | 0.015625 | 453 | 0.03334 | 83 | 0.03388 | 83 | 0.05284 | 85 | 0.06474 | 85 | 0.09152 | 88 | 0.11988 | 88 | 0.15852 | 93 | 0.18683 | 93 | 0.23875 | 101 | 0.26849 | 101 | 0.34108 | 106 | 0.42452 | 106 | 0.53976 | 116 | 0.60783 | 116 | 0.77421
|  |  |  | 454 | 0.011042 | 454 | 0.03334 | 84 | 0.03314 | 84 | 0.05186 | 86 | 0.06336 | 86 | 0.08964 | 89 | 0.11738 | 89 | 0.15514 | 94 | 0.18306 | 94 | 0.2337 | 102 | 0.26339 | 102 | 0.33412 | 107 | 0.41671 | 107 | 0.52885 | 117 | 0.59722 | 117 | 0.75911
|  |  |  | 455 | 0.001 | 455 | 0.03334 | 85 | 0.015625 | 85 | 0.05091 | 87 | 0.06202 | 87 | 0.08782 | 90 | 0.11495 | 90 | 0.15187 | 95 | 0.17587 | 95 | 0.22882 | 103 | 0.25844 | 103 | 0.32739 | 108 | 0.40912 | 108 | 0.51828 | 118 | 0.58689 | 118 | 0.74447
|  |  |  | 500 | 0.001 | 500 | 0.03334 | 86 | 0.015625 | 86 | 0.05 | 88 | 0.06073 | 88 | 0.08607 | 91 | 0.11261 | 91 | 0.14872 | 96 | 0.17243 | 96 | 0.22411 | 104 | 0.25362 | 104 | 0.32086 | 109 | 0.40175 | 109 | 0.50804 | 119 | 0.57683 | 119 | 0.73028
|  |  |  | 501 | 0.001 | 501 | 0.01667 | 87 | 0.015625 | 87 | 0.04912 | 89 | 0.05947 | 89 | 0.08438 | 92 | 0.11033 | 92 | 0.14567 | 97 | 0.1691 | 97 | 0.21954 | 105 | 0.2444 | 105 | 0.31455 | 110 | 0.39457 | 110 | 0.49812 | 120 | 0.56704 | 120 | 0.71652
|  |  |  | 6300 | 0.001 | 6300 | 0.01667 | 88 | 0.015625 | 88 | 0.04826 | 90 | 0.05826 | 90 | 0.08275 | 93 | 0.10813 | 93 | 0.14273 | 98 | 0.16586 | 98 | 0.21513 | 106 | 0.23998 | 106 | 0.30842 | 111 | 0.38759 | 111 | 0.48851 | 121 | 0.55751 | 121 | 0.70316
[8 empty] | 89 | 0.015625 | 89 | 0.04744 | 91 | 0.05708 | 91 | 0.08117 | 94 | 0.10599 | 94 | 0.13988 | 99 | 0.16271 | 99 | 0.21086 | 107 | 0.23568 | 107 | 0.30249 | 112 | 0.3808 | 112 | 0.47918 | 122 | 0.54822 | 122 | 0.6902
[8 empty] | 90 | 0.015625 | 90 | 0.04665 | 92 | 0.05593 | 92 | 0.07964 | 95 | 0.10189 | 95 | 0.13712 | 100 | 0.15966 | 100 | 0.20672 | 108 | 0.2315 | 108 | 0.29674 | 113 | 0.37418 | 113 | 0.47014 | 123 | 0.53917 | 123 | 0.67761
[8 empty] | 91 | 0.015625 | 91 | 0.04588 | 93 | 0.05482 | 93 | 0.07817 | 96 | 0.09993 | 96 | 0.13446 | 101 | 0.15669 | 101 | 0.20271 | 109 | 0.22743 | 109 | 0.29116 | 114 | 0.36775 | 114 | 0.46136 | 124 | 0.53035 | 124 | 0.66539
[8 empty] | 92 | 0.015625 | 92 | 0.04514 | 94 | 0.05375 | 94 | 0.07674 | 97 | 0.09803 | 97 | 0.13188 | 102 | 0.1538 | 102 | 0.19883 | 110 | 0.22347 | 110 | 0.28575 | 115 | 0.35537 | 115 | 0.45284 | 125 | 0.51337 | 125 | 0.65351
[8 empty] | 93 | 0.015625 | 93 | 0.03334 | 95 | 0.05169 | 95 | 0.07536 | 98 | 0.09619 | 98 | 0.12938 | 103 | 0.151 | 103 | 0.19506 | 111 | 0.21961 | 111 | 0.28049 | 116 | 0.34943 | 116 | 0.44456 | 126 | 0.5052 | 126 | 0.64197
[8 empty] | 453 | 0.015625 | 453 | 0.03334 | 96 | 0.0507 | 96 | 0.07402 | 99 | 0.09439 | 99 | 0.12695 | 104 | 0.14827 | 104 | 0.19141 | 112 | 0.21585 | 112 | 0.27539 | 117 | 0.34363 | 117 | 0.43652 | 127 | 0.49722 | 127 | 0.63075
[8 empty] | 454 | 0.011042 | 454 | 0.03334 | 97 | 0.04975 | 97 | 0.07273 | 100 | 0.09265 | 100 | 0.12461 | 105 | 0.14303 | 105 | 0.18787 | 113 | 0.21219 | 113 | 0.27044 | 118 | 0.33798 | 118 | 0.42871 | 128 | 0.48944 | 128 | 0.61983
[8 empty] | 455 | 0.001 | 455 | 0.03334 | 98 | 0.04882 | 98 | 0.07147 | 101 | 0.09095 | 101 | 0.12233 | 106 | 0.14051 | 106 | 0.18443 | 114 | 0.20863 | 114 | 0.26562 | 119 | 0.33247 | 119 | 0.42112 | 129 | 0.48185 | 129 | 0.60922
[8 empty] | 500 | 0.001 | 500 | 0.03334 | 99 | 0.04791 | 99 | 0.07026 | 102 | 0.0893 | 102 | 0.12013 | 107 | 0.13807 | 107 | 0.1811 | 115 | 0.20177 | 115 | 0.26095 | 120 | 0.3271 | 120 | 0.41375 | 130 | 0.47443 | 130 | 0.59889
[8 empty] | 501 | 0.001 | 501 | 0.01667 | 100 | 0.04703 | 100 | 0.06908 | 103 | 0.08769 | 103 | 0.11799 | 108 | 0.13568 | 108 | 0.17786 | 116 | 0.19846 | 116 | 0.2564 | 121 | 0.32186 | 121 | 0.40657 | 131 | 0.46719 | 131 | 0.58883
[8 empty] | 6300 | 0.001 | 6300 | 0.01667 | 101 | 0.04618 | 101 | 0.06793 | 104 | 0.08613 | 104 | 0.11591 | 109 | 0.13336 | 109 | 0.17471 | 117 | 0.19524 | 117 | 0.25198 | 122 | 0.31674 | 122 | 0.39959 | 132 | 0.46012 | 132 | 0.57904
[12 empty] | 102 | 0.04535 | 102 | 0.06682 | 105 | 0.08313 | 105 | 0.11389 | 110 | 0.1311 | 110 | 0.17166 | 118 | 0.1921 | 118 | 0.24768 | 123 | 0.31175 | 123 | 0.3928 | 133 | 0.45322 | 133 | 0.56951
[12 empty] | 103 | 0.04454 | 103 | 0.06575 | 106 | 0.08169 | 106 | 0.11193 | 111 | 0.12889 | 111 | 0.16869 | 119 | 0.18903 | 119 | 0.2435 | 124 | 0.30688 | 124 | 0.38618 | 134 | 0.44647 | 134 | 0.56022
[12 empty] | 104 | 0.04375 | 104 | 0.0647 | 107 | 0.08029 | 107 | 0.11003 | 112 | 0.12674 | 112 | 0.1658 | 120 | 0.18604 | 120 | 0.23943 | 125 | 0.29749 | 125 | 0.37975 | 135 | 0.43988 | 135 | 0.55117
[12 empty] | 105 | 0.04223 | 105 | 0.06369 | 108 | 0.07892 | 108 | 0.10819 | 113 | 0.12465 | 113 | 0.163 | 121 | 0.18312 | 121 | 0.23547 | 126 | 0.29295 | 126 | 0.37348 | 136 | 0.42713 | 136 | 0.54235
[12 empty] | 106 | 0.04151 | 106 | 0.0627 | 109 | 0.07758 | 109 | 0.10639 | 114 | 0.1226 | 114 | 0.16027 | 122 | 0.18027 | 122 | 0.23161 | 127 | 0.28852 | 127 | 0.36737 | 137 | 0.42097 | 137 | 0.53376
[12 empty] | 107 | 0.0408 | 107 | 0.06175 | 110 | 0.07629 | 110 | 0.10465 | 115 | 0.11867 | 115 | 0.15761 | 123 | 0.17749 | 123 | 0.22785 | 128 | 0.28419 | 128 | 0.36143 | 138 | 0.41495 | 138 | 0.52537
[12 empty] | 108 | 0.04011 | 108 | 0.06082 | 111 | 0.07502 | 111 | 0.10295 | 116 | 0.11677 | 116 | 0.15503 | 124 | 0.17477 | 124 | 0.22419 | 129 | 0.27996 | 129 | 0.35563 | 139 | 0.40906 | 139 | 0.5172
[12 empty] | 109 | 0.03943 | 109 | 0.05991 | 112 | 0.07378 | 112 | 0.1013 | 117 | 0.11492 | 117 | 0.15251 | 125 | 0.16952 | 125 | 0.22063 | 130 | 0.27583 | 130 | 0.34998 | 140 | 0.40329 | 140 | 0.50922
[12 empty] | 110 | 0.03878 | 110 | 0.05903 | 113 | 0.07258 | 113 | 0.09969 | 118 | 0.11311 | 118 | 0.15007 | 126 | 0.16698 | 126 | 0.21715 | 131 | 0.27179 | 131 | 0.34447 | 141 | 0.39766 | 141 | 0.50144
[12 empty] | 111 | 0.03814 | 111 | 0.05818 | 114 | 0.0714 | 114 | 0.09813 | 119 | 0.11134 | 119 | 0.14768 | 127 | 0.1645 | 127 | 0.21377 | 132 | 0.26784 | 132 | 0.3391 | 142 | 0.39214 | 142 | 0.49385
[12 empty] | 112 | 0.03751 | 112 | 0.05735 | 115 | 0.06914 | 115 | 0.09661 | 120 | 0.10962 | 120 | 0.14536 | 128 | 0.16208 | 128 | 0.21046 | 133 | 0.26397 | 133 | 0.33386 | 143 | 0.38673 | 143 | 0.48643
[12 empty] | 113 | 0.0369 | 113 | 0.05654 | 116 | 0.06804 | 116 | 0.09513 | 121 | 0.10794 | 121 | 0.1431 | 129 | 0.15971 | 129 | 0.20724 | 134 | 0.26019 | 134 | 0.32874 | 144 | 0.38145 | 144 | 0.47919
[12 empty] | 114 | 0.03631 | 114 | 0.05575 | 117 | 0.06698 | 117 | 0.09369 | 122 | 0.10629 | 122 | 0.14089 | 130 | 0.15739 | 130 | 0.2041 | 135 | 0.25649 | 135 | 0.32375 | 145 | 0.3712 | 145 | 0.47212
[12 empty] | 115 | 0.03516 | 115 | 0.05498 | 118 | 0.06593 | 118 | 0.09229 | 123 | 0.10468 | 123 | 0.13874 | 131 | 0.15512 | 131 | 0.20103 | 136 | 0.24933 | 136 | 0.31888 | 146 | 0.36623 | 146 | 0.46522
[12 empty] | 116 | 0.03461 | 116 | 0.05423 | 119 | 0.06492 | 119 | 0.09092 | 124 | 0.10311 | 124 | 0.13665 | 132 | 0.15291 | 132 | 0.19804 | 137 | 0.24587 | 137 | 0.31413 | 147 | 0.36137 | 147 | 0.45847
[12 empty] | 117 | 0.03407 | 117 | 0.05351 | 120 | 0.06392 | 120 | 0.08958 | 125 | 0.10008 | 125 | 0.1346 | 133 | 0.15074 | 133 | 0.19512 | 138 | 0.24247 | 138 | 0.30949 | 148 | 0.3566 | 148 | 0.45188
[12 empty] | 118 | 0.03354 | 118 | 0.0528 | 121 | 0.06295 | 121 | 0.08829 | 126 | 0.09861 | 126 | 0.13261 | 134 | 0.14861 | 134 | 0.19227 | 139 | 0.23915 | 139 | 0.30495 | 149 | 0.35193 | 149 | 0.44543
[12 empty] | 119 | 0.03303 | 119 | 0.05211 | 122 | 0.062 | 122 | 0.08702 | 127 | 0.09717 | 127 | 0.13067 | 135 | 0.14654 | 135 | 0.18949 | 140 | 0.2359 | 140 | 0.30052 | 150 | 0.34735 | 150 | 0.43913
[12 empty] | 120 | 0.015625 | 120 | 0.05143 | 123 | 0.06107 | 123 | 0.08578 | 128 | 0.09577 | 128 | 0.12877 | 136 | 0.14251 | 136 | 0.18677 | 141 | 0.23271 | 141 | 0.29619 | 151 | 0.34287 | 151 | 0.43297
[12 empty] | 121 | 0.015625 | 121 | 0.05078 | 124 | 0.06017 | 124 | 0.08458 | 129 | 0.09439 | 129 | 0.12692 | 137 | 0.14056 | 137 | 0.18411 | 142 | 0.22959 | 142 | 0.29196 | 152 | 0.33847 | 152 | 0.42695
[12 empty] | 122 | 0.015625 | 122 | 0.05014 | 125 | 0.05841 | 125 | 0.0834 | 130 | 0.09305 | 130 | 0.12511 | 138 | 0.13865 | 138 | 0.18152 | 143 | 0.22653 | 143 | 0.28783 | 153 | 0.33416 | 153 | 0.42106
[12 empty] | 123 | 0.015625 | 123 | 0.04951 | 126 | 0.05756 | 126 | 0.08225 | 131 | 0.09173 | 131 | 0.12334 | 139 | 0.13678 | 139 | 0.17898 | 144 | 0.22354 | 144 | 0.28379 | 154 | 0.32993 | 154 | 0.41529
[12 empty] | 124 | 0.015625 | 124 | 0.0489 | 127 | 0.05673 | 127 | 0.08114 | 132 | 0.09045 | 132 | 0.12162 | 140 | 0.13495 | 140 | 0.1765 | 145 | 0.21772 | 145 | 0.27984 | 155 | 0.32578 | 155 | 0.40966
[12 empty] | 125 | 0.015625 | 125 | 0.04831 | 128 | 0.05592 | 128 | 0.08004 | 133 | 0.08919 | 133 | 0.11994 | 141 | 0.13315 | 141 | 0.17408 | 146 | 0.2149 | 146 | 0.27597 | 156 | 0.31773 | 156 | 0.40414
[12 empty] | 126 | 0.015625 | 126 | 0.04773 | 129 | 0.05513 | 129 | 0.07898 | 134 | 0.08795 | 134 | 0.11829 | 142 | 0.13139 | 142 | 0.17171 | 147 | 0.21213 | 147 | 0.27219 | 157 | 0.31381 | 157 | 0.39873
[12 empty] | 127 | 0.015625 | 127 | 0.04716 | 130 | 0.05435 | 130 | 0.07793 | 135 | 0.08674 | 135 | 0.11668 | 143 | 0.12967 | 143 | 0.16939 | 148 | 0.20942 | 148 | 0.26849 | 158 | 0.30997 | 158 | 0.39345
[12 empty] | 128 | 0.015625 | 128 | 0.04661 | 131 | 0.05359 | 131 | 0.07692 | 136 | 0.0844 | 136 | 0.11511 | 144 | 0.12797 | 144 | 0.16712 | 149 | 0.20676 | 149 | 0.26487 | 159 | 0.3062 | 159 | 0.38827
[12 empty] | 129 | 0.015625 | 129 | 0.04607 | 132 | 0.05284 | 132 | 0.07592 | 137 | 0.08326 | 137 | 0.11358 | 145 | 0.12469 | 145 | 0.16491 | 150 | 0.20415 | 150 | 0.26133 | 160 | 0.3025 | 160 | 0.3832
[12 empty] | 130 | 0.015625 | 130 | 0.04554 | 133 | 0.05211 | 133 | 0.07495 | 138 | 0.08215 | 138 | 0.11208 | 146 | 0.1231 | 146 | 0.16274 | 151 | 0.20159 | 151 | 0.25787 | 161 | 0.29887 | 161 | 0.37823
[12 empty] | 131 | 0.015625 | 131 | 0.04503 | 134 | 0.0514 | 134 | 0.074 | 139 | 0.08106 | 139 | 0.11061 | 147 | 0.12154 | 147 | 0.16061 | 152 | 0.19908 | 152 | 0.25447 | 162 | 0.2953 | 162 | 0.37337
[12 empty] | 132 | 0.015625 | 132 | 0.03334 | 135 | 0.05069 | 135 | 0.07307 | 140 | 0.07999 | 140 | 0.10917 | 148 | 0.12 | 148 | 0.15854 | 153 | 0.19662 | 153 | 0.25115 | 163 | 0.2918 | 163 | 0.3686
[12 empty] | 453 | 0.015625 | 453 | 0.03334 | 136 | 0.04934 | 136 | 0.07217 | 141 | 0.07894 | 141 | 0.10777 | 149 | 0.1185 | 149 | 0.1565 | 154 | 0.1942 | 154 | 0.2479 | 164 | 0.28837 | 164 | 0.36393
[12 empty] | 454 | 0.011042 | 454 | 0.03334 | 137 | 0.04868 | 137 | 0.07128 | 142 | 0.07792 | 142 | 0.10639 | 150 | 0.11702 | 150 | 0.15451 | 155 | 0.19183 | 155 | 0.24471 | 165 | 0.28167 | 165 | 0.35935
[12 empty] | 455 | 0.001 | 455 | 0.03334 | 138 | 0.04803 | 138 | 0.07041 | 143 | 0.07691 | 143 | 0.10505 | 151 | 0.11557 | 151 | 0.15256 | 156 | 0.18722 | 156 | 0.24159 | 166 | 0.27842 | 166 | 0.35487
[12 empty] | 500 | 0.001 | 500 | 0.03334 | 139 | 0.0474 | 139 | 0.06956 | 144 | 0.07592 | 144 | 0.10373 | 152 | 0.11415 | 152 | 0.15065 | 157 | 0.18497 | 157 | 0.23853 | 167 | 0.27522 | 167 | 0.35047
[12 empty] | 501 | 0.001 | 501 | 0.01667 | 140 | 0.04678 | 140 | 0.06873 | 145 | 0.074 | 145 | 0.10245 | 153 | 0.11276 | 153 | 0.14878 | 158 | 0.18277 | 158 | 0.23554 | 168 | 0.27207 | 168 | 0.34616
[12 empty] | 6300 | 0.001 | 6300 | 0.01667 | 141 | 0.04617 | 141 | 0.06792 | 146 | 0.07307 | 146 | 0.10119 | 154 | 0.11139 | 154 | 0.14695 | 159 | 0.1806 | 159 | 0.2326 | 169 | 0.26898 | 169 | 0.34193
[16 empty] | 142 | 0.04558 | 142 | 0.06713 | 147 | 0.07216 | 147 | 0.09995 | 155 | 0.11005 | 155 | 0.14515 | 160 | 0.17848 | 160 | 0.22972 | 170 | 0.26595 | 170 | 0.33778
[16 empty] | 143 | 0.04499 | 143 | 0.06635 | 148 | 0.07126 | 148 | 0.09874 | 156 | 0.10743 | 156 | 0.14339 | 161 | 0.17639 | 161 | 0.2269 | 171 | 0.26296 | 171 | 0.33372
[16 empty] | 144 | 0.04442 | 144 | 0.06559 | 149 | 0.07038 | 149 | 0.09756 | 157 | 0.10616 | 157 | 0.14167 | 162 | 0.17434 | 162 | 0.22413 | 172 | 0.26003 | 172 | 0.32973
[16 empty] | 145 | 0.0433 | 145 | 0.06484 | 150 | 0.06951 | 150 | 0.0964 | 158 | 0.10491 | 158 | 0.13997 | 163 | 0.17233 | 163 | 0.22142 | 173 | 0.25714 | 173 | 0.32581
[16 empty] | 146 | 0.04276 | 146 | 0.06411 | 151 | 0.06866 | 151 | 0.09526 | 159 | 0.10368 | 159 | 0.13832 | 164 | 0.17035 | 164 | 0.21876 | 174 | 0.25431 | 174 | 0.32197
[16 empty] | 147 | 0.04223 | 147 | 0.0634 | 152 | 0.06783 | 152 | 0.09415 | 160 | 0.10247 | 160 | 0.13669 | 165 | 0.16649 | 165 | 0.21615 | 175 | 0.24878 | 175 | 0.3182
[16 empty] | 148 | 0.04171 | 148 | 0.06269 | 153 | 0.06701 | 153 | 0.09306 | 161 | 0.10129 | 161 | 0.1351 | 166 | 0.16461 | 166 | 0.21359 | 176 | 0.24608 | 176 | 0.3145
[16 empty] | 149 | 0.0412 | 149 | 0.06201 | 154 | 0.06621 | 154 | 0.09199 | 162 | 0.10012 | 162 | 0.13354 | 167 | 0.16276 | 167 | 0.21108 | 177 | 0.24343 | 177 | 0.31087
[16 empty] | 150 | 0.04069 | 150 | 0.06134 | 155 | 0.06542 | 155 | 0.09094 | 163 | 0.09898 | 163 | 0.132 | 168 | 0.16095 | 168 | 0.20862 | 178 | 0.24082 | 178 | 0.3073
[16 empty] | 151 | 0.0402 | 151 | 0.06068 | 156 | 0.06389 | 156 | 0.08992 | 164 | 0.09785 | 164 | 0.1305 | 169 | 0.15916 | 169 | 0.2062 | 179 | 0.23826 | 179 | 0.3038
[16 empty] | 152 | 0.03972 | 152 | 0.06003 | 157 | 0.06314 | 157 | 0.08891 | 165 | 0.09566 | 165 | 0.12902 | 170 | 0.15741 | 170 | 0.20383 | 180 | 0.23573 | 180 | 0.30037
[16 empty] | 153 | 0.03924 | 153 | 0.0594 | 158 | 0.06241 | 158 | 0.08792 | 166 | 0.09459 | 166 | 0.12757 | 171 | 0.15568 | 171 | 0.2015 | 181 | 0.23325 | 181 | 0.29699
[16 empty] | 154 | 0.03877 | 154 | 0.05878 | 159 | 0.06168 | 159 | 0.08695 | 167 | 0.09354 | 167 | 0.12615 | 172 | 0.15398 | 172 | 0.19922 | 182 | 0.2308 | 182 | 0.29367
[16 empty] | 155 | 0.03831 | 155 | 0.05817 | 160 | 0.06097 | 160 | 0.086 | 168 | 0.09251 | 168 | 0.12476 | 173 | 0.15231 | 173 | 0.19697 | 183 | 0.2284 | 183 | 0.29042
[16 empty] | 156 | 0.03742 | 156 | 0.05758 | 161 | 0.06028 | 161 | 0.08507 | 169 | 0.09149 | 169 | 0.12339 | 174 | 0.15067 | 174 | 0.19477 | 184 | 0.22603 | 184 | 0.28722
[16 empty] | 157 | 0.03699 | 157 | 0.05699 | 162 | 0.05959 | 162 | 0.08416 | 170 | 0.0905 | 170 | 0.12205 | 175 | 0.14746 | 175 | 0.1926 | 185 | 0.22141 | 185 | 0.28407
[16 empty] | 158 | 0.03656 | 158 | 0.05642 | 163 | 0.05892 | 163 | 0.08326 | 171 | 0.08951 | 171 | 0.12073 | 176 | 0.1459 | 176 | 0.19048 | 186 | 0.21915 | 186 | 0.28098
[16 empty] | 159 | 0.03614 | 159 | 0.05585 | 164 | 0.05826 | 164 | 0.08238 | 172 | 0.08855 | 172 | 0.11943 | 177 | 0.14436 | 177 | 0.18839 | 187 | 0.21692 | 187 | 0.27795
[16 empty] | 160 | 0.03573 | 160 | 0.0553 | 165 | 0.05697 | 165 | 0.08151 | 173 | 0.0876 | 173 | 0.11816 | 178 | 0.14285 | 178 | 0.18634 | 188 | 0.21473 | 188 | 0.27496
[16 empty] | 161 | 0.03532 | 161 | 0.05476 | 166 | 0.05634 | 166 | 0.08066 | 174 | 0.08666 | 174 | 0.11691 | 179 | 0.14136 | 179 | 0.18433 | 189 | 0.21258 | 189 | 0.27203
[16 empty] | 162 | 0.03492 | 162 | 0.05423 | 167 | 0.05572 | 167 | 0.07983 | 175 | 0.08483 | 175 | 0.11568 | 180 | 0.13989 | 180 | 0.18235 | 190 | 0.21046 | 190 | 0.26914
[16 empty] | 163 | 0.03453 | 163 | 0.05371 | 168 | 0.05511 | 168 | 0.07901 | 176 | 0.08394 | 176 | 0.11447 | 181 | 0.13844 | 181 | 0.1804 | 191 | 0.20836 | 191 | 0.26631
[16 empty] | 164 | 0.03414 | 164 | 0.0532 | 169 | 0.05451 | 169 | 0.07821 | 177 | 0.08306 | 177 | 0.11329 | 182 | 0.13702 | 182 | 0.17849 | 192 | 0.2063 | 192 | 0.26352
[16 empty] | 165 | 0.03339 | 165 | 0.05269 | 170 | 0.05392 | 170 | 0.07742 | 178 | 0.0822 | 178 | 0.11212 | 183 | 0.13562 | 183 | 0.17661 | 193 | 0.20428 | 193 | 0.26078
[16 empty] | 166 | 0.03302 | 166 | 0.0522 | 171 | 0.05334 | 171 | 0.07665 | 179 | 0.08135 | 179 | 0.11098 | 184 | 0.13424 | 184 | 0.17476 | 194 | 0.20228 | 194 | 0.25808
[16 empty] | 167 | 0.015625 | 167 | 0.05172 | 172 | 0.05277 | 172 | 0.07589 | 180 | 0.08051 | 180 | 0.10985 | 185 | 0.13155 | 185 | 0.17295 | 195 | 0.19837 | 195 | 0.25543
[16 empty] | 168 | 0.015625 | 168 | 0.05124 | 173 | 0.05221 | 173 | 0.07514 | 181 | 0.07969 | 181 | 0.10875 | 186 | 0.13023 | 186 | 0.17116 | 196 | 0.19646 | 196 | 0.25282
[16 empty] | 169 | 0.015625 | 169 | 0.05077 | 174 | 0.05166 | 174 | 0.07441 | 182 | 0.07888 | 182 | 0.10766 | 187 | 0.12894 | 187 | 0.16941 | 197 | 0.19457 | 197 | 0.25026
[16 empty] | 170 | 0.015625 | 170 | 0.05031 | 175 | 0.05058 | 175 | 0.07368 | 183 | 0.07808 | 183 | 0.10659 | 188 | 0.12766 | 188 | 0.16768 | 198 | 0.19272 | 198 | 0.24773
[16 empty] | 171 | 0.015625 | 171 | 0.04986 | 176 | 0.05006 | 176 | 0.07297 | 184 | 0.07729 | 184 | 0.10554 | 189 | 0.1264 | 189 | 0.16598 | 199 | 0.19089 | 199 | 0.24525
[16 empty] | 172 | 0.015625 | 172 | 0.04942 | 177 | 0.04954 | 177 | 0.07228 | 185 | 0.07576 | 185 | 0.10451 | 190 | 0.12516 | 190 | 0.16431 | 200 | 0.18908 | 200 | 0.2428
[16 empty] | 173 | 0.015625 | 173 | 0.04899 | 178 | 0.04903 | 178 | 0.07159 | 186 | 0.075 | 186 | 0.10349 | 191 | 0.12394 | 191 | 0.16267 | 201 | 0.18731 | 201 | 0.2404
[16 empty] | 174 | 0.015625 | 174 | 0.04856 | 179 | 0.04853 | 179 | 0.07092 | 187 | 0.07426 | 187 | 0.1025 | 192 | 0.12274 | 192 | 0.16105 | 202 | 0.18556 | 202 | 0.23803
[16 empty] | 175 | 0.015625 | 175 | 0.04814 | 180 | 0.04803 | 180 | 0.07026 | 188 | 0.07353 | 188 | 0.10151 | 193 | 0.12155 | 193 | 0.15946 | 203 | 0.18383 | 203 | 0.2357
[16 empty] | 176 | 0.015625 | 176 | 0.04773 | 181 | 0.04755 | 181 | 0.06961 | 189 | 0.07282 | 189 | 0.10055 | 194 | 0.12039 | 194 | 0.1579 | 204 | 0.18212 | 204 | 0.23341
[16 empty] | 177 | 0.015625 | 177 | 0.04732 | 182 | 0.04707 | 182 | 0.06897 | 190 | 0.07211 | 190 | 0.0996 | 195 | 0.1181 | 195 | 0.15636 | 205 | 0.17879 | 205 | 0.23115
[16 empty] | 178 | 0.015625 | 178 | 0.04692 | 183 | 0.04659 | 183 | 0.06834 | 191 | 0.07141 | 191 | 0.09866 | 196 | 0.11698 | 196 | 0.15485 | 206 | 0.17716 | 206 | 0.22892
[16 empty] | 179 | 0.015625 | 179 | 0.04653 | 184 | 0.04613 | 184 | 0.06772 | 192 | 0.07072 | 192 | 0.09774 | 197 | 0.11588 | 197 | 0.15336 | 207 | 0.17555 | 207 | 0.22673
[16 empty] | 180 | 0.015625 | 180 | 0.04614 | 185 | 0.04522 | 185 | 0.06711 | 193 | 0.07004 | 193 | 0.09683 | 198 | 0.11479 | 198 | 0.15189 | 208 | 0.17396 | 208 | 0.22458
[16 empty] | 181 | 0.015625 | 181 | 0.04576 | 186 | 0.04478 | 186 | 0.06651 | 194 | 0.06938 | 194 | 0.09594 | 199 | 0.11372 | 199 | 0.15044 | 209 | 0.17239 | 209 | 0.22246
[16 empty] | 182 | 0.015625 | 182 | 0.04539 | 187 | 0.04434 | 187 | 0.06592 | 195 | 0.06807 | 195 | 0.09506 | 200 | 0.11266 | 200 | 0.14902 | 210 | 0.17085 | 210 | 0.22036
[16 empty] | 183 | 0.015625 | 183 | 0.04502 | 188 | 0.04391 | 188 | 0.06534 | 196 | 0.06743 | 196 | 0.0942 | 201 | 0.11162 | 201 | 0.14762 | 211 | 0.16932 | 211 | 0.2183
[16 empty] | 184 | 0.015625 | 184 | 0.03334 | 189 | 0.04348 | 189 | 0.06477 | 197 | 0.0668 | 197 | 0.09335 | 202 | 0.11059 | 202 | 0.14624 | 212 | 0.16782 | 212 | 0.21628
[16 empty] | 453 | 0.015625 | 453 | 0.03334 | 190 | 0.04306 | 190 | 0.06421 | 198 | 0.06618 | 198 | 0.09251 | 203 | 0.10958 | 203 | 0.14489 | 213 | 0.16634 | 213 | 0.21428
[16 empty] | 454 | 0.011042 | 454 | 0.03334 | 191 | 0.04265 | 191 | 0.06366 | 199 | 0.06556 | 199 | 0.09169 | 204 | 0.10858 | 204 | 0.14355 | 214 | 0.16487 | 214 | 0.21231
[16 empty] | 455 | 0.001 | 455 | 0.03334 | 192 | 0.04224 | 192 | 0.06312 | 200 | 0.06496 | 200 | 0.09088 | 205 | 0.10662 | 205 | 0.14223 | 215 | 0.162 | 215 | 0.21037
[16 empty] | 500 | 0.001 | 500 | 0.03334 | 193 | 0.04184 | 193 | 0.06258 | 201 | 0.06436 | 201 | 0.09008 | 206 | 0.10567 | 206 | 0.14094 | 216 | 0.1606 | 216 | 0.20846
[16 empty] | 501 | 0.001 | 501 | 0.01667 | 194 | 0.04144 | 194 | 0.06206 | 202 | 0.06377 | 202 | 0.08929 | 207 | 0.10472 | 207 | 0.13966 | 217 | 0.15921 | 217 | 0.20657
[16 empty] | 6300 | 0.001 | 6300 | 0.01667 | 195 | 0.04067 | 195 | 0.06154 | 203 | 0.06319 | 203 | 0.08852 | 208 | 0.10379 | 208 | 0.1384 | 218 | 0.15784 | 218 | 0.20472
[20 empty] | 196 | 0.04029 | 196 | 0.06103 | 204 | 0.06262 | 204 | 0.08776 | 209 | 0.10287 | 209 | 0.13716 | 219 | 0.15649 | 219 | 0.20289
[20 empty] | 197 | 0.03991 | 197 | 0.06053 | 205 | 0.0615 | 205 | 0.087 | 210 | 0.10196 | 210 | 0.13594 | 220 | 0.15515 | 220 | 0.20108
[20 empty] | 198 | 0.03955 | 198 | 0.06003 | 206 | 0.06095 | 206 | 0.08626 | 211 | 0.10106 | 211 | 0.13474 | 221 | 0.15383 | 221 | 0.19931
[20 empty] | 199 | 0.03918 | 199 | 0.05955 | 207 | 0.06041 | 207 | 0.08553 | 212 | 0.10018 | 212 | 0.13355 | 222 | 0.15253 | 222 | 0.19756
[20 empty] | 200 | 0.03882 | 200 | 0.05907 | 208 | 0.05987 | 208 | 0.08482 | 213 | 0.09931 | 213 | 0.13239 | 223 | 0.15125 | 223 | 0.19583
[20 empty] | 201 | 0.03847 | 201 | 0.05859 | 209 | 0.05935 | 209 | 0.08411 | 214 | 0.09844 | 214 | 0.13123 | 224 | 0.14998 | 224 | 0.19412
[20 empty] | 202 | 0.03812 | 202 | 0.05813 | 210 | 0.05883 | 210 | 0.08341 | 215 | 0.09675 | 215 | 0.1301 | 225 | 0.1475 | 225 | 0.19245
[20 empty] | 203 | 0.03778 | 203 | 0.05767 | 211 | 0.05831 | 211 | 0.08272 | 216 | 0.09593 | 216 | 0.12898 | 226 | 0.14628 | 226 | 0.19079
[20 empty] | 204 | 0.03744 | 204 | 0.05722 | 212 | 0.0578 | 212 | 0.08204 | 217 | 0.09511 | 217 | 0.12788 | 227 | 0.14507 | 227 | 0.18916
[20 empty] | 205 | 0.03677 | 205 | 0.05678 | 213 | 0.0573 | 213 | 0.08138 | 218 | 0.0943 | 218 | 0.12679 | 228 | 0.14388 | 228 | 0.18755
[20 empty] | 206 | 0.03645 | 206 | 0.05634 | 214 | 0.05681 | 214 | 0.08072 | 219 | 0.09351 | 219 | 0.12572 | 229 | 0.1427 | 229 | 0.18596
[20 empty] | 207 | 0.03612 | 207 | 0.05591 | 215 | 0.05584 | 215 | 0.08007 | 220 | 0.09272 | 220 | 0.12466 | 230 | 0.14154 | 230 | 0.18439
[20 empty] | 208 | 0.03581 | 208 | 0.05548 | 216 | 0.05537 | 216 | 0.07943 | 221 | 0.09194 | 221 | 0.12362 | 231 | 0.1404 | 231 | 0.18285
[20 empty] | 209 | 0.03549 | 209 | 0.05506 | 217 | 0.0549 | 217 | 0.0788 | 222 | 0.09118 | 222 | 0.12259 | 232 | 0.13926 | 232 | 0.18132
[20 empty] | 210 | 0.03518 | 210 | 0.05465 | 218 | 0.05443 | 218 | 0.07818 | 223 | 0.09042 | 223 | 0.12158 | 233 | 0.13815 | 233 | 0.17982
[20 empty] | 211 | 0.03488 | 211 | 0.05424 | 219 | 0.05398 | 219 | 0.07756 | 224 | 0.08967 | 224 | 0.12058 | 234 | 0.13704 | 234 | 0.17834
[20 empty] | 212 | 0.03458 | 212 | 0.05384 | 220 | 0.05353 | 220 | 0.07696 | 225 | 0.0882 | 225 | 0.1196 | 235 | 0.13595 | 235 | 0.17687
[20 empty] | 213 | 0.03428 | 213 | 0.05344 | 221 | 0.05308 | 221 | 0.07636 | 226 | 0.08748 | 226 | 0.11862 | 236 | 0.1338 | 236 | 0.17543
[20 empty] | 214 | 0.03399 | 214 | 0.05305 | 222 | 0.05264 | 222 | 0.07577 | 227 | 0.08677 | 227 | 0.11767 | 237 | 0.13275 | 237 | 0.174
[20 empty] | 215 | 0.03341 | 215 | 0.05267 | 223 | 0.05221 | 223 | 0.07519 | 228 | 0.08607 | 228 | 0.11672 | 238 | 0.13171 | 238 | 0.1726
[20 empty] | 216 | 0.03313 | 216 | 0.05229 | 224 | 0.05178 | 224 | 0.07462 | 229 | 0.08537 | 229 | 0.11579 | 239 | 0.13068 | 239 | 0.17121
[20 empty] | 217 | 0.015625 | 217 | 0.05191 | 225 | 0.05093 | 225 | 0.07406 | 230 | 0.08469 | 230 | 0.11487 | 240 | 0.12967 | 240 | 0.16984
[20 empty] | 218 | 0.015625 | 218 | 0.05155 | 226 | 0.05052 | 226 | 0.0735 | 231 | 0.08401 | 231 | 0.11396 | 241 | 0.12866 | 241 | 0.16849
[20 empty] | 219 | 0.015625 | 219 | 0.05118 | 227 | 0.05011 | 227 | 0.07295 | 232 | 0.08334 | 232 | 0.11306 | 242 | 0.12767 | 242 | 0.16715
[20 empty] | 220 | 0.015625 | 220 | 0.05082 | 228 | 0.04971 | 228 | 0.07241 | 233 | 0.08268 | 233 | 0.11218 | 243 | 0.12669 | 243 | 0.16583
[20 empty] | 221 | 0.015625 | 221 | 0.05047 | 229 | 0.04931 | 229 | 0.07187 | 234 | 0.08203 | 234 | 0.11131 | 244 | 0.12572 | 244 | 0.16453
[20 empty] | 222 | 0.015625 | 222 | 0.05012 | 230 | 0.04891 | 230 | 0.07135 | 235 | 0.08138 | 235 | 0.11044 | 245 | 0.12381 | 245 | 0.16325
[20 empty] | 223 | 0.015625 | 223 | 0.04978 | 231 | 0.04853 | 231 | 0.07083 | 236 | 0.08011 | 236 | 0.10959 | 246 | 0.12288 | 246 | 0.16198
[20 empty] | 224 | 0.015625 | 224 | 0.04944 | 232 | 0.04814 | 232 | 0.07031 | 237 | 0.07949 | 237 | 0.10875 | 247 | 0.12195 | 247 | 0.16073
[20 empty] | 225 | 0.015625 | 225 | 0.0491 | 233 | 0.04776 | 233 | 0.0698 | 238 | 0.07887 | 238 | 0.10793 | 248 | 0.12103 | 248 | 0.1595
[20 empty] | 226 | 0.015625 | 226 | 0.04877 | 234 | 0.04739 | 234 | 0.0693 | 239 | 0.07826 | 239 | 0.10711 | 249 | 0.12013 | 249 | 0.15828
[20 empty] | 227 | 0.015625 | 227 | 0.04845 | 235 | 0.04701 | 235 | 0.06881 | 240 | 0.07766 | 240 | 0.1063 | 250 | 0.11923 | 250 | 0.15707
[20 empty] | 228 | 0.015625 | 228 | 0.04812 | 236 | 0.04629 | 236 | 0.06832 | 241 | 0.07707 | 241 | 0.10551 | 251 | 0.11835 | 251 | 0.15588
[20 empty] | 229 | 0.015625 | 229 | 0.04781 | 237 | 0.04593 | 237 | 0.06784 | 242 | 0.07648 | 242 | 0.10472 | 252 | 0.11747 | 252 | 0.1547
[20 empty] | 230 | 0.015625 | 230 | 0.04749 | 238 | 0.04557 | 238 | 0.06737 | 243 | 0.0759 | 243 | 0.10394 | 253 | 0.11661 | 253 | 0.15354
[20 empty] | 231 | 0.015625 | 231 | 0.04718 | 239 | 0.04522 | 239 | 0.0669 | 244 | 0.07532 | 244 | 0.10318 | 254 | 0.11575 | 254 | 0.1524
[20 empty] | 232 | 0.015625 | 232 | 0.04688 | 240 | 0.04488 | 240 | 0.06643 | 245 | 0.07419 | 245 | 0.10242 | 255 | 0.11491 | 255 | 0.15126
[20 empty] | 233 | 0.015625 | 233 | 0.04658 | 241 | 0.04453 | 241 | 0.06598 | 246 | 0.07364 | 246 | 0.10167 | 256 | 0.11324 | 256 | 0.15015
[20 empty] | 234 | 0.015625 | 234 | 0.04628 | 242 | 0.0442 | 242 | 0.06553 | 247 | 0.07309 | 247 | 0.10093 | 257 | 0.11242 | 257 | 0.14904
[20 empty] | 235 | 0.015625 | 235 | 0.04599 | 243 | 0.04386 | 243 | 0.06508 | 248 | 0.07255 | 248 | 0.1002 | 258 | 0.11161 | 258 | 0.14795
[20 empty] | 236 | 0.015625 | 236 | 0.0457 | 244 | 0.04353 | 244 | 0.06464 | 249 | 0.07201 | 249 | 0.09948 | 259 | 0.11081 | 259 | 0.14687
[20 empty] | 237 | 0.015625 | 237 | 0.04541 | 245 | 0.04288 | 245 | 0.06421 | 250 | 0.07148 | 250 | 0.09877 | 260 | 0.11002 | 260 | 0.1458
[20 empty] | 238 | 0.015625 | 238 | 0.04513 | 246 | 0.04256 | 246 | 0.06378 | 251 | 0.07095 | 251 | 0.09807 | 261 | 0.10924 | 261 | 0.14475
[20 empty] | 239 | 0.015625 | 239 | 0.03334 | 247 | 0.04225 | 247 | 0.06335 | 252 | 0.07043 | 252 | 0.09737 | 262 | 0.10846 | 262 | 0.14371
[20 empty] | 453 | 0.015625 | 453 | 0.03334 | 248 | 0.04193 | 248 | 0.06293 | 253 | 0.06992 | 253 | 0.09669 | 263 | 0.1077 | 263 | 0.14268
[20 empty] | 454 | 0.011042 | 454 | 0.03334 | 249 | 0.04163 | 249 | 0.06252 | 254 | 0.06941 | 254 | 0.09601 | 264 | 0.10694 | 264 | 0.14167
[20 empty] | 455 | 0.001 | 455 | 0.03334 | 250 | 0.04132 | 250 | 0.06211 | 255 | 0.06891 | 255 | 0.09534 | 265 | 0.10544 | 265 | 0.14066
[20 empty] | 500 | 0.001 | 500 | 0.03334 | 251 | 0.04102 | 251 | 0.06171 | 256 | 0.06792 | 256 | 0.09468 | 266 | 0.10471 | 266 | 0.13967
[20 empty] | 501 | 0.001 | 501 | 0.01667 | 252 | 0.04072 | 252 | 0.06131 | 257 | 0.06744 | 257 | 0.09403 | 267 | 0.10398 | 267 | 0.13869
[20 empty] | 6300 | 0.001 | 6300 | 0.01667 | 253 | 0.04042 | 253 | 0.06091 | 258 | 0.06696 | 258 | 0.09338 | 268 | 0.10326 | 268 | 0.13772
[24 empty] | 254 | 0.04013 | 254 | 0.06053 | 259 | 0.06648 | 259 | 0.09274 | 269 | 0.10255 | 269 | 0.13676
[24 empty] | 255 | 0.03984 | 255 | 0.06014 | 260 | 0.06601 | 260 | 0.09211 | 270 | 0.10184 | 270 | 0.13581
[24 empty] | 256 | 0.03927 | 256 | 0.05976 | 261 | 0.06554 | 261 | 0.09149 | 271 | 0.10115 | 271 | 0.13488
[24 empty] | 257 | 0.03899 | 257 | 0.05939 | 262 | 0.06508 | 262 | 0.09087 | 272 | 0.10046 | 272 | 0.13395
[24 empty] | 258 | 0.03872 | 258 | 0.05901 | 263 | 0.06463 | 263 | 0.09026 | 273 | 0.015625 | 273 | 0.13303
[24 empty] | 259 | 0.03844 | 259 | 0.05865 | 264 | 0.06418 | 264 | 0.08966 | 274 | 0.015625 | 274 | 0.13213
[24 empty] | 260 | 0.03817 | 260 | 0.05829 | 265 | 0.06329 | 265 | 0.08907 | 275 | 0.015625 | 275 | 0.13123
[24 empty] | 261 | 0.0379 | 261 | 0.05793 | 266 | 0.06285 | 266 | 0.08848 | 276 | 0.015625 | 276 | 0.13035
[24 empty] | 262 | 0.03764 | 262 | 0.05757 | 267 | 0.06242 | 267 | 0.0879 | 277 | 0.015625 | 277 | 0.12947
[24 empty] | 263 | 0.03738 | 263 | 0.05722 | 268 | 0.06199 | 268 | 0.08732 | 278 | 0.015625 | 278 | 0.12861
[24 empty] | 264 | 0.03712 | 264 | 0.05688 | 269 | 0.06157 | 269 | 0.08676 | 279 | 0.015625 | 279 | 0.12775
[24 empty] | 265 | 0.0366 | 265 | 0.05653 | 270 | 0.06115 | 270 | 0.08619 | 280 | 0.015625 | 280 | 0.12691
[24 empty] | 266 | 0.03635 | 266 | 0.0562 | 271 | 0.06073 | 271 | 0.08564 | 281 | 0.015625 | 281 | 0.12607
[24 empty] | 267 | 0.0361 | 267 | 0.05586 | 272 | 0.06032 | 272 | 0.08509 | 282 | 0.015625 | 282 | 0.12524
[24 empty] | 268 | 0.03586 | 268 | 0.05553 | 273 | 0.015625 | 273 | 0.08455 | 283 | 0.015625 | 283 | 0.12442
[24 empty] | 269 | 0.03561 | 269 | 0.05521 | 274 | 0.015625 | 274 | 0.08401 | 284 | 0.015625 | 284 | 0.12361
[24 empty] | 270 | 0.03537 | 270 | 0.05488 | 275 | 0.015625 | 275 | 0.08348 | 285 | 0.015625 | 285 | 0.12281
[24 empty] | 271 | 0.03513 | 271 | 0.05456 | 276 | 0.015625 | 276 | 0.08295 | 286 | 0.015625 | 286 | 0.12202
[24 empty] | 272 | 0.0349 | 272 | 0.05425 | 277 | 0.015625 | 277 | 0.08243 | 287 | 0.015625 | 287 | 0.12124
[24 empty] | 273 | 0.015625 | 273 | 0.05393 | 278 | 0.015625 | 278 | 0.08192 | 288 | 0.015625 | 288 | 0.12046
[24 empty] | 274 | 0.015625 | 274 | 0.05363 | 279 | 0.015625 | 279 | 0.08141 | 289 | 0.015625 | 289 | 0.1197
[24 empty] | 275 | 0.015625 | 275 | 0.05332 | 280 | 0.015625 | 280 | 0.08091 | 290 | 0.015625 | 290 | 0.11894
[24 empty] | 276 | 0.015625 | 276 | 0.05302 | 281 | 0.015625 | 281 | 0.08041 | 291 | 0.015625 | 291 | 0.11819
[24 empty] | 277 | 0.015625 | 277 | 0.05272 | 282 | 0.015625 | 282 | 0.07992 | 292 | 0.015625 | 292 | 0.11744
[24 empty] | 278 | 0.015625 | 278 | 0.05242 | 283 | 0.015625 | 283 | 0.07944 | 293 | 0.015625 | 293 | 0.11671
[24 empty] | 279 | 0.015625 | 279 | 0.05213 | 284 | 0.015625 | 284 | 0.07896 | 294 | 0.015625 | 294 | 0.11598
[24 empty] | 280 | 0.015625 | 280 | 0.05184 | 285 | 0.015625 | 285 | 0.07848 | 295 | 0.015625 | 295 | 0.11526
[24 empty] | 281 | 0.015625 | 281 | 0.05156 | 286 | 0.015625 | 286 | 0.07801 | 296 | 0.015625 | 296 | 0.11455
[24 empty] | 282 | 0.015625 | 282 | 0.05127 | 287 | 0.015625 | 287 | 0.07754 | 297 | 0.015625 | 297 | 0.11384
[24 empty] | 283 | 0.015625 | 283 | 0.05099 | 288 | 0.015625 | 288 | 0.07708 | 298 | 0.015625 | 298 | 0.11315
[24 empty] | 284 | 0.015625 | 284 | 0.05072 | 289 | 0.015625 | 289 | 0.07663 | 299 | 0.015625 | 299 | 0.11246
[24 empty] | 285 | 0.015625 | 285 | 0.05044 | 290 | 0.015625 | 290 | 0.07618 | 300 | 0.015625 | 300 | 0.03334
[24 empty] | 286 | 0.015625 | 286 | 0.05017 | 291 | 0.015625 | 291 | 0.07573 | 453 | 0.015625 | 453 | 0.03334
[24 empty] | 287 | 0.015625 | 287 | 0.0499 | 292 | 0.015625 | 292 | 0.07529 | 454 | 0.011042 | 454 | 0.03334
[24 empty] | 288 | 0.015625 | 288 | 0.04964 | 293 | 0.015625 | 293 | 0.07485 | 455 | 0.001 | 455 | 0.03334
[24 empty] | 289 | 0.015625 | 289 | 0.04938 | 294 | 0.015625 | 294 | 0.07442 | 500 | 0.001 | 500 | 0.03334
[24 empty] | 290 | 0.015625 | 290 | 0.04912 | 295 | 0.015625 | 295 | 0.07399 | 501 | 0.001 | 501 | 0.01667
[24 empty] | 291 | 0.015625 | 291 | 0.04886 | 296 | 0.015625 | 296 | 0.07357 | 6300 | 0.001 | 6300 | 0.01667
[24 empty] | 292 | 0.015625 | 292 | 0.0486 | 297 | 0.015625 | 297 | 0.07315
[24 empty] | 293 | 0.015625 | 293 | 0.04835 | 298 | 0.015625 | 298 | 0.07273
[24 empty] | 294 | 0.015625 | 294 | 0.0481 | 299 | 0.015625 | 299 | 0.07232
[24 empty] | 295 | 0.015625 | 295 | 0.04786 | 300 | 0.015625 | 300 | 0.03334
[24 empty] | 296 | 0.015625 | 296 | 0.04761 | 453 | 0.015625 | 453 | 0.03334
[24 empty] | 297 | 0.015625 | 297 | 0.04737 | 454 | 0.011042 | 454 | 0.03334
[24 empty] | 298 | 0.015625 | 298 | 0.04713 | 455 | 0.001 | 455 | 0.03334
[24 empty] | 299 | 0.015625 | 299 | 0.0469 | 500 | 0.001 | 500 | 0.03334
[24 empty] | 300 | 0.015625 | 300 | 0.03334 | 501 | 0.001 | 501 | 0.01667
[24 empty] | 453 | 0.015625 | 453 | 0.03334 | 6300 | 0.001 | 6300 | 0.01667
[24 empty] | 454 | 0.011042 | 454 | 0.03334
[24 empty] | 455 | 0.001 | 455 | 0.03334
[24 empty] | 500 | 0.001 | 500 | 0.03334
[24 empty] | 501 | 0.001 | 501 | 0.01667
[24 empty] | 6300 | 0.001 | 6300 | 0.01667

## S&C "KS" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "KS" Speed | [11 empty] | S&C "KS" Speed | [11 empty] | S&C "KS" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023
Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information.
2KS |  |  |  | 3KS |  |  |  | 5KS |  |  |  | 7KS |  |  |  | 10KS |  |  |  | 15KS |  |  |  | 20KS
Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s
4 | 77.1064 | 4 | 301.35 | 6 | 100.914 | 6 | 301.35 | 10 | 161.233 | 10 | 302.442 | 14 | 161.275 | 14 | 256.423 | 20 | 119.954 | 20 | 248.069 | 30 | 120.5385 | 30 | 301.35 | 40 | 100.871 | 40 | 301.536
5 | 46.8696 | 5 | 77.1184 | 7 | 47.4062 | 7 | 100.926 | 11 | 102.089 | 11 | 161.245 | 15 | 95.9248 | 15 | 161.287 | 21 | 91.5597 | 21 | 155.228 | 31 | 106.936 | 31 | 210.867 | 41 | 80.0658 | 41 | 202.94
6 | 31.7276 | 6 | 46.8816 | 8 | 35.5166 | 8 | 47.4182 | 12 | 63.5514 | 12 | 102.101 | 16 | 60.8436 | 16 | 95.9368 | 22 | 79.8656 | 22 | 119.966 | 32 | 82.3015 | 32 | 134.153 | 42 | 73.6897 | 42 | 151.098
7 | 26.1719 | 7 | 31.7396 | 9 | 27.5049 | 9 | 35.5286 | 13 | 48.3201 | 13 | 63.5634 | 17 | 47.0154 | 17 | 74.6838 | 23 | 68.1715 | 23 | 91.5717 | 33 | 65.4069 | 33 | 120.5505 | 43 | 67.3136 | 43 | 119.575
8 | 16.9981 | 8 | 26.1839 | 10 | 21.6785 | 10 | 27.5169 | 14 | 38.3535 | 14 | 48.3321 | 18 | 36.147 | 18 | 60.8556 | 24 | 53.5641 | 24 | 79.8776 | 34 | 59.4855 | 34 | 106.948 | 44 | 60.9375 | 44 | 100.883
9 | 13.3974 | 9 | 17.0101 | 11 | 17.3357 | 11 | 21.6905 | 15 | 28.9001 | 15 | 38.3655 | 19 | 31.8687 | 19 | 47.0274 | 25 | 40.047 | 25 | 68.1835 | 35 | 53.5641 | 35 | 82.3135 | 45 | 47.1713 | 45 | 80.0778
10 | 9.0224 | 10 | 13.4094 | 12 | 15.528 | 12 | 17.3477 | 16 | 23.1697 | 16 | 28.9121 | 20 | 27.5904 | 20 | 36.159 | 26 | 35.5302 | 26 | 53.5761 | 36 | 41.4447 | 36 | 65.4189 | 46 | 43.545 | 46 | 73.7017
11 | 6.8582 | 11 | 9.0344 | 13 | 13.7202 | 13 | 15.5399 | 17 | 18.5014 | 17 | 26.0469 | 21 | 21.4553 | 21 | 31.8807 | 27 | 31.0134 | 27 | 46.8175 | 37 | 38.1062 | 37 | 59.4975 | 47 | 39.9188 | 47 | 67.3256
12 | 4.981 | 12 | 6.8702 | 14 | 12.3687 | 14 | 13.7322 | 18 | 16.5348 | 18 | 23.1817 | 22 | 19.6561 | 22 | 27.6024 | 28 | 28.4931 | 28 | 40.059 | 38 | 31.9583 | 38 | 53.5761 | 48 | 37.909 | 48 | 60.9495
13 | 3.8177 | 13 | 4.9931 | 15 | 11.0171 | 15 | 12.3806 | 19 | 14.5682 | 19 | 18.5134 | 23 | 17.8568 | 23 | 21.4673 | 29 | 25.9728 | 29 | 35.5422 | 39 | 30.102 | 39 | 44.7951 | 49 | 35.8992 | 49 | 50.8095
14 | 2.9997 | 14 | 3.8297 | 16 | 8.7647 | 16 | 11.0291 | 20 | 13.224 | 20 | 16.5468 | 24 | 16.0576 | 24 | 19.6681 | 30 | 23.4525 | 30 | 31.0254 | 40 | 28.2457 | 40 | 41.4567 | 50 | 33.8893 | 50 | 47.1833
15 | 2.3206 | 15 | 3.0117 | 17 | 8.1649 | 17 | 9.9029 | 21 | 11.8798 | 21 | 14.5802 | 25 | 13.1774 | 25 | 17.8688 | 31 | 22.0554 | 31 | 28.5051 | 41 | 26.3894 | 41 | 38.1182 | 51 | 31.8795 | 51 | 43.557
16 | 1.6664 | 16 | 2.3326 | 18 | 7.5652 | 18 | 8.7767 | 22 | 9.8537 | 22 | 13.236 | 26 | 12.2577 | 26 | 16.0696 | 32 | 20.6582 | 32 | 25.9848 | 42 | 24.3296 | 42 | 31.9703 | 52 | 29.8697 | 52 | 39.9308
17 | 1.5065 | 17 | 2.0055 | 19 | 6.9655 | 19 | 8.1769 | 23 | 9.2531 | 23 | 11.8918 | 27 | 11.338 | 27 | 14.6295 | 33 | 19.2611 | 33 | 23.4645 | 43 | 22.2698 | 43 | 30.114 | 53 | 27.3721 | 53 | 37.921
18 | 1.3466 | 18 | 1.6784 | 20 | 4.7889 | 20 | 7.5772 | 24 | 8.6525 | 24 | 9.8657 | 28 | 10.4183 | 28 | 13.1894 | 34 | 17.8639 | 34 | 22.0674 | 44 | 21.0995 | 44 | 28.2577 | 54 | 24.8745 | 54 | 35.9112
19 | 1.1867 | 19 | 1.5185 | 21 | 4.2203 | 21 | 6.9775 | 25 | 5.6851 | 25 | 9.2651 | 29 | 9.8815 | 29 | 12.2697 | 35 | 16.8244 | 35 | 20.6702 | 45 | 18.759 | 45 | 26.4014 | 55 | 22.8937 | 55 | 33.9013
20 | 1.0731 | 20 | 1.3586 | 22 | 3.6515 | 22 | 4.801 | 26 | 5.0497 | 26 | 8.6645 | 30 | 9.3447 | 30 | 11.35 | 36 | 14.7455 | 36 | 19.2731 | 46 | 17.5887 | 46 | 24.3416 | 56 | 21.9032 | 56 | 31.8915
21 | 0.95956 | 21 | 1.1987 | 23 | 3.2678 | 23 | 4.2322 | 27 | 4.4143 | 27 | 6.8251 | 31 | 8.8079 | 31 | 10.4303 | 37 | 13.706 | 37 | 17.8759 | 47 | 16.5721 | 47 | 22.2818 | 57 | 20.9128 | 57 | 29.8817
22 | 0.84599 | 22 | 1.0851 | 24 | 2.884 | 24 | 3.6635 | 28 | 3.713 | 28 | 5.6971 | 32 | 8.2711 | 32 | 9.8935 | 38 | 13.0463 | 38 | 16.8364 | 48 | 15.5554 | 48 | 21.1115 | 58 | 19.9224 | 58 | 27.3841
23 | 0.7862 | 23 | 0.97156 | 25 | 2.3351 | 25 | 3.2798 | 29 | 3.4672 | 29 | 5.0617 | 33 | 7.845 | 33 | 9.3567 | 39 | 12.3866 | 39 | 15.797 | 49 | 14.5388 | 49 | 19.9413 | 59 | 19.0841 | 59 | 24.8865
24 | 0.72642 | 24 | 0.85799 | 26 | 2.1851 | 26 | 2.896 | 30 | 3.2215 | 30 | 4.4263 | 34 | 7.4188 | 34 | 8.8199 | 40 | 11.7269 | 40 | 14.7575 | 50 | 13.7689 | 50 | 18.771 | 60 | 18.2457 | 60 | 23.8961
25 | 0.60685 | 25 | 0.7982 | 27 | 2.0351 | 27 | 2.6215 | 31 | 3.0536 | 31 | 3.725 | 35 | 6.9926 | 35 | 8.2831 | 41 | 11.0672 | 41 | 13.718 | 51 | 12.999 | 51 | 17.6007 | 61 | 17.4074 | 61 | 22.9057
26 | 0.56915 | 26 | 0.73842 | 28 | 1.885 | 28 | 2.3471 | 32 | 2.8857 | 32 | 3.4792 | 36 | 6.2609 | 36 | 7.857 | 42 | 10.4075 | 42 | 13.0583 | 52 | 12.229 | 52 | 16.5841 | 62 | 16.569 | 62 | 21.9152
27 | 0.53146 | 27 | 0.67863 | 29 | 1.735 | 29 | 2.1971 | 33 | 2.7178 | 33 | 3.2335 | 37 | 5.9554 | 37 | 7.4308 | 43 | 10.0061 | 43 | 12.3986 | 53 | 11.4591 | 53 | 15.5674 | 63 | 15.7307 | 63 | 20.9248
28 | 0.49376 | 28 | 0.61885 | 30 | 1.6269 | 30 | 2.0471 | 34 | 2.5477 | 34 | 3.0656 | 38 | 5.6498 | 38 | 7.0046 | 44 | 9.6047 | 44 | 11.7389 | 54 | 11.0874 | 54 | 14.5508 | 64 | 14.8923 | 64 | 19.9344
29 | 0.45606 | 29 | 0.58115 | 31 | 1.5188 | 31 | 1.897 | 35 | 2.3776 | 35 | 2.8977 | 39 | 5.3442 | 39 | 6.5785 | 45 | 8.8019 | 45 | 11.0792 | 55 | 10.3439 | 55 | 13.7809 | 65 | 13.7399 | 65 | 19.0961
30 | 0.43704 | 30 | 0.54346 | 32 | 1.4107 | 32 | 1.747 | 36 | 2.1238 | 36 | 2.7298 | 40 | 5.0693 | 40 | 6.2729 | 46 | 8.4006 | 46 | 10.4195 | 56 | 9.9722 | 56 | 13.0109 | 66 | 13.1636 | 66 | 18.2577
31 | 0.41802 | 31 | 0.50576 | 33 | 1.3026 | 33 | 1.6389 | 37 | 2.0401 | 37 | 2.5597 | 41 | 4.7943 | 41 | 5.9673 | 47 | 8.0612 | 47 | 10.0181 | 57 | 9.6004 | 57 | 12.241 | 67 | 12.5874 | 67 | 17.4194
32 | 0.39899 | 32 | 0.46806 | 34 | 1.2396 | 34 | 1.5308 | 38 | 1.9565 | 38 | 2.3896 | 42 | 4.5193 | 42 | 5.6618 | 48 | 7.7218 | 48 | 9.6167 | 58 | 9.2479 | 58 | 11.4711 | 68 | 12.0112 | 68 | 16.581
33 | 0.37997 | 33 | 0.44904 | 35 | 1.1768 | 35 | 1.4227 | 39 | 1.8728 | 39 | 2.2195 | 43 | 4.2762 | 43 | 5.3562 | 49 | 7.3825 | 49 | 9.2153 | 59 | 8.8954 | 59 | 11.0994 | 69 | 11.6215 | 69 | 15.7426
34 | 0.36095 | 34 | 0.43002 | 36 | 1.051 | 36 | 1.3146 | 40 | 1.7055 | 40 | 2.1358 | 44 | 4.0332 | 44 | 5.0812 | 50 | 7.0431 | 50 | 8.8139 | 60 | 8.5428 | 60 | 10.7276 | 70 | 11.2318 | 70 | 14.9043
35 | 0.34443 | 35 | 0.41099 | 37 | 0.98807 | 37 | 1.2516 | 41 | 1.6253 | 41 | 2.0521 | 45 | 3.6242 | 45 | 4.8063 | 51 | 6.7038 | 51 | 8.4125 | 61 | 8.1903 | 61 | 10.3559 | 71 | 10.8421 | 71 | 14.3281
36 | 0.3114 | 36 | 0.39197 | 38 | 0.94625 | 38 | 1.1888 | 42 | 1.5451 | 42 | 1.9685 | 46 | 3.4583 | 46 | 4.5313 | 52 | 6.5025 | 52 | 8.0732 | 62 | 7.8378 | 62 | 9.9842 | 72 | 10.4524 | 72 | 13.7519
37 | 0.29489 | 37 | 0.37295 | 39 | 0.90444 | 39 | 1.1259 | 43 | 1.4649 | 43 | 1.8848 | 47 | 3.2924 | 47 | 4.2882 | 53 | 6.3012 | 53 | 7.7339 | 63 | 7.6135 | 63 | 9.6124 | 73 | 10.0627 | 73 | 13.1756
38 | 0.27837 | 38 | 0.35643 | 40 | 0.86263 | 40 | 1.063 | 44 | 1.3847 | 44 | 1.7175 | 48 | 3.1265 | 48 | 4.0452 | 54 | 6.0999 | 54 | 7.3945 | 64 | 7.3892 | 64 | 9.2599 | 74 | 9.7782 | 74 | 12.5994
39 | 0.26728 | 39 | 0.33992 | 41 | 0.82082 | 41 | 1.0001 | 45 | 1.2572 | 45 | 1.6373 | 49 | 2.985 | 49 | 3.8022 | 55 | 5.6973 | 55 | 7.0552 | 65 | 6.9407 | 65 | 8.9074 | 75 | 9.4938 | 75 | 12.0232
40 | 0.25619 | 40 | 0.3234 | 42 | 0.77901 | 42 | 0.95825 | 46 | 1.2098 | 46 | 1.5571 | 50 | 2.8434 | 50 | 3.6362 | 56 | 5.496 | 56 | 6.7158 | 66 | 6.7164 | 66 | 8.5548 | 76 | 8.9249 | 76 | 11.6335
41 | 0.24509 | 41 | 0.30689 | 43 | 0.7372 | 43 | 0.91644 | 47 | 1.1625 | 47 | 1.4769 | 51 | 2.7019 | 51 | 3.4703 | 57 | 5.2947 | 57 | 6.5145 | 67 | 6.4921 | 67 | 8.2023 | 77 | 8.5938 | 77 | 11.2438
42 | 0.234 | 42 | 0.29037 | 44 | 0.71202 | 44 | 0.87463 | 48 | 1.1151 | 48 | 1.3967 | 52 | 2.5604 | 52 | 3.3044 | 58 | 5.1379 | 58 | 6.3132 | 68 | 6.3242 | 68 | 7.8498 | 78 | 8.2626 | 78 | 10.8541
43 | 0.22291 | 43 | 0.27928 | 45 | 0.66166 | 45 | 0.83282 | 49 | 1.0678 | 49 | 1.3165 | 53 | 2.4655 | 53 | 3.1385 | 59 | 4.9811 | 59 | 6.1119 | 69 | 6.1563 | 69 | 7.6255 | 79 | 7.9315 | 79 | 10.4644
44 | 0.21182 | 44 | 0.26819 | 46 | 0.63648 | 46 | 0.79101 | 50 | 1.0204 | 50 | 1.2692 | 54 | 2.3706 | 54 | 2.997 | 60 | 4.8243 | 60 | 5.9106 | 70 | 5.9883 | 70 | 7.4012 | 80 | 7.7354 | 80 | 10.0747
45 | 0.19823 | 45 | 0.25709 | 47 | 0.6113 | 47 | 0.7492 | 51 | 0.97309 | 51 | 1.2218 | 55 | 2.1808 | 55 | 2.8554 | 61 | 4.6676 | 61 | 5.7093 | 71 | 5.8204 | 71 | 7.1769 | 81 | 7.5392 | 81 | 9.7903
46 | 0.19144 | 46 | 0.246 | 48 | 0.58612 | 48 | 0.72402 | 52 | 0.92574 | 52 | 1.1745 | 56 | 2.086 | 56 | 2.7139 | 62 | 4.5108 | 62 | 5.508 | 72 | 5.6525 | 72 | 6.9527 | 82 | 7.343 | 82 | 9.5058
47 | 0.18465 | 47 | 0.23491 | 49 | 0.56095 | 49 | 0.69884 | 53 | 0.89939 | 53 | 1.1271 | 57 | 2.0209 | 57 | 2.5724 | 63 | 4.354 | 63 | 5.3067 | 73 | 5.4846 | 73 | 6.7284 | 83 | 7.1469 | 83 | 9.2213
48 | 0.17786 | 48 | 0.22382 | 50 | 0.54076 | 50 | 0.67366 | 54 | 0.87304 | 54 | 1.0798 | 58 | 1.9559 | 58 | 2.4775 | 64 | 4.2481 | 64 | 5.1499 | 74 | 5.3167 | 74 | 6.5041 | 84 | 6.9507 | 84 | 8.9369
49 | 0.17107 | 49 | 0.21703 | 51 | 0.52058 | 51 | 0.64848 | 55 | 0.82033 | 55 | 1.0324 | 59 | 1.8908 | 59 | 2.3826 | 65 | 4.0364 | 65 | 4.9931 | 75 | 5.206 | 75 | 6.3362 | 85 | 6.669 | 85 | 8.6058
50 | 0.16427 | 50 | 0.21023 | 52 | 0.50039 | 52 | 0.6233 | 56 | 0.79398 | 56 | 0.98509 | 60 | 1.8257 | 60 | 2.2877 | 66 | 3.9306 | 66 | 4.8363 | 76 | 4.9846 | 76 | 6.1683 | 86 | 6.5281 | 86 | 8.2746
51 | 0.15748 | 51 | 0.20344 | 53 | 0.48021 | 53 | 0.59812 | 57 | 0.76763 | 57 | 0.93774 | 61 | 1.7607 | 61 | 2.1928 | 67 | 3.8247 | 67 | 4.6796 | 77 | 4.874 | 77 | 6.0004 | 87 | 6.3872 | 87 | 7.9435
52 | 0.15069 | 52 | 0.19665 | 54 | 0.46002 | 54 | 0.57295 | 58 | 0.74128 | 58 | 0.91139 | 62 | 1.6956 | 62 | 2.098 | 68 | 3.7188 | 68 | 4.5228 | 78 | 4.7633 | 78 | 5.8324 | 88 | 6.2463 | 88 | 7.7473
53 | 0.14687 | 53 | 0.18986 | 55 | 0.4288 | 55 | 0.55276 | 59 | 0.71492 | 59 | 0.88504 | 63 | 1.6305 | 63 | 2.0329 | 69 | 3.613 | 69 | 4.366 | 79 | 4.6526 | 79 | 5.6645 | 89 | 6.1055 | 89 | 7.5512
54 | 0.14305 | 54 | 0.18307 | 56 | 0.41777 | 56 | 0.53258 | 60 | 0.68857 | 60 | 0.85868 | 64 | 1.5909 | 64 | 1.9679 | 70 | 3.5071 | 70 | 4.2601 | 80 | 4.5419 | 80 | 5.4966 | 90 | 5.9646 | 90 | 7.355
55 | 0.1354 | 55 | 0.17627 | 57 | 0.40674 | 57 | 0.51239 | 61 | 0.66222 | 61 | 0.83233 | 65 | 1.5117 | 65 | 1.9028 | 71 | 3.4329 | 71 | 4.1543 | 81 | 4.4313 | 81 | 5.3286 | 91 | 5.8418 | 91 | 7.1589
56 | 0.13158 | 56 | 0.16948 | 58 | 0.3957 | 58 | 0.49221 | 62 | 0.64776 | 62 | 0.80598 | 66 | 1.4721 | 66 | 1.8377 | 72 | 3.3588 | 72 | 4.0484 | 82 | 4.3384 | 82 | 5.218 | 92 | 5.719 | 92 | 6.9627
57 | 0.12776 | 57 | 0.16269 | 59 | 0.38467 | 59 | 0.47202 | 63 | 0.6333 | 63 | 0.77963 | 67 | 1.4325 | 67 | 1.7727 | 73 | 3.2846 | 73 | 3.9426 | 83 | 4.2455 | 83 | 5.1073 | 93 | 5.5961 | 93 | 6.8218
58 | 0.12394 | 58 | 0.15887 | 60 | 0.37363 | 60 | 0.45184 | 64 | 0.61883 | 64 | 0.75328 | 68 | 1.3929 | 68 | 1.7076 | 74 | 3.2104 | 74 | 3.8367 | 84 | 4.1526 | 84 | 4.9966 | 94 | 5.4733 | 94 | 6.681
59 | 0.12012 | 59 | 0.15505 | 61 | 0.3626 | 61 | 0.4408 | 65 | 0.58991 | 65 | 0.72692 | 69 | 1.3533 | 69 | 1.6425 | 75 | 3.1362 | 75 | 3.7308 | 85 | 3.9668 | 85 | 4.886 | 95 | 5.2277 | 95 | 6.5401
60 | 0.1163 | 60 | 0.15123 | 62 | 0.35156 | 62 | 0.42977 | 66 | 0.57545 | 66 | 0.70057 | 70 | 1.3136 | 70 | 1.6029 | 76 | 2.9879 | 76 | 3.625 | 86 | 3.874 | 86 | 4.7753 | 96 | 5.1049 | 96 | 6.3992
61 | 0.11248 | 61 | 0.1474 | 63 | 0.34053 | 63 | 0.41874 | 67 | 0.56099 | 67 | 0.67422 | 71 | 1.274 | 71 | 1.5633 | 77 | 2.9137 | 77 | 3.5191 | 87 | 3.7811 | 87 | 4.6646 | 97 | 4.9821 | 97 | 6.2584
62 | 0.10866 | 62 | 0.14358 | 64 | 0.3295 | 64 | 0.4077 | 68 | 0.54653 | 68 | 0.65976 | 72 | 1.2344 | 72 | 1.5237 | 78 | 2.8396 | 78 | 3.4449 | 88 | 3.6882 | 88 | 4.554 | 98 | 4.8792 | 98 | 6.1175
63 | 0.10626 | 63 | 0.13976 | 65 | 0.31111 | 65 | 0.39667 | 69 | 0.53207 | 69 | 0.6453 | 73 | 1.1948 | 73 | 1.4841 | 79 | 2.7892 | 79 | 3.3708 | 89 | 3.5953 | 89 | 4.4433 | 99 | 4.7763 | 99 | 5.9766
64 | 0.10386 | 64 | 0.13594 | 66 | 0.30376 | 66 | 0.38563 | 70 | 0.51761 | 70 | 0.63083 | 74 | 1.1552 | 74 | 1.4445 | 80 | 2.7389 | 80 | 3.2966 | 90 | 3.536 | 90 | 4.3504 | 100 | 4.6734 | 100 | 5.8538
65 | 0.09906 | 65 | 0.13212 | 67 | 0.29641 | 67 | 0.3746 | 71 | 0.50315 | 71 | 0.61637 | 75 | 1.1303 | 75 | 1.4049 | 81 | 2.6885 | 81 | 3.2224 | 91 | 3.4768 | 91 | 4.2575 | 101 | 4.5705 | 101 | 5.731
66 | 0.09666 | 66 | 0.1283 | 68 | 0.28906 | 68 | 0.36356 | 72 | 0.48868 | 72 | 0.60191 | 76 | 1.0805 | 76 | 1.3653 | 82 | 2.6382 | 82 | 3.1482 | 92 | 3.4175 | 92 | 4.1646 | 102 | 4.4676 | 102 | 5.6082
67 | 0.09426 | 67 | 0.12448 | 69 | 0.28171 | 69 | 0.35253 | 73 | 0.47422 | 73 | 0.58745 | 77 | 1.0556 | 77 | 1.3256 | 83 | 2.5878 | 83 | 3.0741 | 93 | 3.3582 | 93 | 4.0717 | 103 | 4.3777 | 103 | 5.4853
68 | 0.09186 | 68 | 0.12066 | 70 | 0.27436 | 70 | 0.3415 | 74 | 0.45976 | 74 | 0.57299 | 78 | 1.0308 | 78 | 1.286 | 84 | 2.5375 | 84 | 2.9999 | 94 | 3.2989 | 94 | 3.9788 | 104 | 4.2878 | 104 | 5.3625
69 | 0.08946 | 69 | 0.11826 | 71 | 0.26701 | 71 | 0.33046 | 75 | 0.4453 | 75 | 0.55853 | 79 | 1.0059 | 79 | 1.2464 | 85 | 2.4367 | 85 | 2.9257 | 95 | 3.1804 | 95 | 3.886 | 105 | 4.1081 | 105 | 5.2397
70 | 0.08706 | 70 | 0.11586 | 72 | 0.25965 | 72 | 0.32311 | 76 | 0.41638 | 76 | 0.54407 | 80 | 0.98099 | 80 | 1.2068 | 86 | 2.3864 | 86 | 2.8516 | 96 | 3.1211 | 96 | 3.7931 | 106 | 4.0182 | 106 | 5.1169
71 | 0.08466 | 71 | 0.11346 | 73 | 0.2523 | 73 | 0.31576 | 77 | 0.40899 | 77 | 0.52961 | 81 | 0.95611 | 81 | 1.1672 | 87 | 2.3229 | 87 | 2.8012 | 97 | 3.0618 | 97 | 3.7002 | 107 | 3.95 | 107 | 4.9941
72 | 0.08226 | 72 | 0.11106 | 74 | 0.24669 | 74 | 0.30841 | 78 | 0.40161 | 78 | 0.51515 | 82 | 0.93122 | 82 | 1.1423 | 88 | 2.2593 | 88 | 2.7509 | 98 | 3.0025 | 98 | 3.6073 | 108 | 3.8818 | 108 | 4.8912
73 | 0.07986 | 73 | 0.10866 | 75 | 0.24107 | 75 | 0.30106 | 79 | 0.39422 | 79 | 0.50068 | 83 | 0.90633 | 83 | 1.1174 | 89 | 2.1958 | 89 | 2.7005 | 99 | 2.9433 | 99 | 3.548 | 109 | 3.8135 | 109 | 4.7883
74 | 0.07746 | 74 | 0.10626 | 76 | 0.22984 | 76 | 0.29371 | 80 | 0.38684 | 80 | 0.48622 | 84 | 0.88145 | 84 | 1.0925 | 90 | 2.1323 | 90 | 2.6502 | 100 | 2.884 | 100 | 3.4888 | 110 | 3.7453 | 110 | 4.6854
75 | 0.07594 | 75 | 0.10386 | 77 | 0.22422 | 77 | 0.28636 | 81 | 0.37945 | 81 | 0.47176 | 85 | 0.84117 | 85 | 1.0676 | 91 | 2.0688 | 91 | 2.5998 | 101 | 2.8381 | 101 | 3.4295 | 111 | 3.6771 | 111 | 4.5825
76 | 0.07291 | 76 | 0.10146 | 78 | 0.21861 | 78 | 0.27901 | 82 | 0.37206 | 82 | 0.4573 | 86 | 0.82578 | 86 | 1.0428 | 92 | 2.025 | 92 | 2.5495 | 102 | 2.7922 | 102 | 3.3702 | 112 | 3.6088 | 112 | 4.4796
77 | 0.07139 | 77 | 0.09906 | 79 | 0.21299 | 79 | 0.27165 | 83 | 0.36468 | 83 | 0.44284 | 87 | 0.81038 | 87 | 1.0179 | 93 | 1.9813 | 93 | 2.4991 | 103 | 2.7463 | 103 | 3.3109 | 113 | 3.5406 | 113 | 4.3897
78 | 0.06987 | 78 | 0.09666 | 80 | 0.20738 | 80 | 0.2643 | 84 | 0.35729 | 84 | 0.42838 | 88 | 0.79499 | 88 | 0.99299 | 94 | 1.9376 | 94 | 2.4487 | 104 | 2.7004 | 104 | 3.2517 | 114 | 3.4724 | 114 | 4.2998
79 | 0.06836 | 79 | 0.09426 | 81 | 0.20176 | 81 | 0.25869 | 85 | 0.34252 | 85 | 0.42099 | 89 | 0.7796 | 89 | 0.96811 | 95 | 1.8501 | 95 | 2.3984 | 105 | 2.6085 | 105 | 3.1924 | 115 | 3.3537 | 115 | 4.21
80 | 0.06684 | 80 | 0.09186 | 82 | 0.19806 | 82 | 0.25307 | 86 | 0.33514 | 86 | 0.41361 | 90 | 0.76421 | 90 | 0.94322 | 96 | 1.8064 | 96 | 2.3349 | 106 | 2.5626 | 106 | 3.1331 | 116 | 3.2944 | 116 | 4.1201
81 | 0.06532 | 81 | 0.08946 | 83 | 0.19436 | 83 | 0.24746 | 87 | 0.32775 | 87 | 0.40622 | 91 | 0.74881 | 91 | 0.91833 | 97 | 1.7627 | 97 | 2.2713 | 107 | 2.5167 | 107 | 3.0738 | 117 | 3.235 | 117 | 4.0302
82 | 0.06381 | 82 | 0.08794 | 84 | 0.19067 | 84 | 0.24184 | 88 | 0.32037 | 88 | 0.39884 | 92 | 0.73342 | 92 | 0.89345 | 98 | 1.7189 | 98 | 2.2078 | 108 | 2.4708 | 108 | 3.0145 | 118 | 3.1757 | 118 | 3.962
83 | 0.06229 | 83 | 0.08642 | 85 | 0.18327 | 85 | 0.23622 | 89 | 0.31298 | 89 | 0.39145 | 93 | 0.71803 | 93 | 0.86856 | 99 | 1.6822 | 99 | 2.1443 | 109 | 2.4249 | 109 | 2.9553 | 119 | 3.1164 | 119 | 3.8938
84 | 0.06077 | 84 | 0.08491 | 86 | 0.17957 | 86 | 0.23061 | 90 | 0.3056 | 90 | 0.38406 | 94 | 0.70264 | 94 | 0.85317 | 100 | 1.6455 | 100 | 2.0808 | 110 | 2.379 | 110 | 2.896 | 120 | 3.057 | 120 | 3.8255
85 | 0.05774 | 85 | 0.08339 | 87 | 0.17587 | 87 | 0.22499 | 91 | 0.29821 | 91 | 0.37668 | 95 | 0.67185 | 95 | 0.83778 | 101 | 1.6088 | 101 | 2.037 | 111 | 2.346 | 111 | 2.8501 | 121 | 2.9977 | 121 | 3.7573
86 | 0.05622 | 86 | 0.08187 | 88 | 0.17218 | 88 | 0.21938 | 92 | 0.29082 | 92 | 0.36929 | 96 | 0.65646 | 96 | 0.82238 | 102 | 1.5721 | 102 | 1.9933 | 112 | 2.313 | 112 | 2.8042 | 122 | 2.9558 | 122 | 3.6891
87 | 0.05471 | 87 | 0.08036 | 89 | 0.16848 | 89 | 0.21376 | 93 | 0.28344 | 93 | 0.36191 | 97 | 0.64107 | 97 | 0.80699 | 103 | 1.5355 | 103 | 1.9496 | 113 | 2.2799 | 113 | 2.7583 | 123 | 2.9139 | 123 | 3.6208
88 | 0.05037 | 88 | 0.07884 | 90 | 0.16478 | 90 | 0.21006 | 94 | 0.27605 | 94 | 0.35452 | 98 | 0.63145 | 98 | 0.7916 | 104 | 1.4988 | 104 | 1.9059 | 114 | 2.2469 | 114 | 2.7124 | 124 | 2.872 | 124 | 3.5526
89 | 0.04602 | 89 | 0.07732 | 91 | 0.16108 | 91 | 0.20636 | 95 | 0.26825 | 95 | 0.34714 | 99 | 0.62184 | 99 | 0.77621 | 105 | 1.4254 | 105 | 1.8621 | 115 | 2.1809 | 115 | 2.6665 | 125 | 2.7881 | 125 | 3.4844
90 | 0.04168 | 90 | 0.07581 | 92 | 0.15738 | 92 | 0.20267 | 96 | 0.26435 | 96 | 0.33975 | 100 | 0.61223 | 100 | 0.76081 | 106 | 1.3887 | 106 | 1.8184 | 116 | 2.1479 | 116 | 2.6205 | 126 | 2.7462 | 126 | 3.425
91 | 0.03734 | 91 | 0.07429 | 93 | 0.1546 | 93 | 0.19897 | 97 | 0.26044 | 97 | 0.33237 | 101 | 0.60261 | 101 | 0.74542 | 107 | 1.352 | 107 | 1.7747 | 117 | 2.1149 | 117 | 2.5746 | 127 | 2.7043 | 127 | 3.3657
92 | 0.015625 | 92 | 0.07277 | 94 | 0.15181 | 94 | 0.19527 | 98 | 0.25654 | 98 | 0.32498 | 102 | 0.593 | 102 | 0.73003 | 108 | 1.3272 | 108 | 1.7309 | 118 | 2.0819 | 118 | 2.5287 | 128 | 2.6624 | 128 | 3.3064
93 | 0.015625 | 93 | 0.07126 | 95 | 0.14623 | 95 | 0.19157 | 99 | 0.25264 | 99 | 0.3176 | 103 | 0.58338 | 103 | 0.71464 | 109 | 1.3024 | 109 | 1.6942 | 119 | 2.0488 | 119 | 2.4828 | 129 | 2.6205 | 129 | 3.247
94 | 0.015625 | 94 | 0.06974 | 96 | 0.14344 | 96 | 0.18787 | 100 | 0.24874 | 100 | 0.31021 | 104 | 0.57377 | 104 | 0.69924 | 110 | 1.2776 | 110 | 1.6575 | 120 | 2.0158 | 120 | 2.4369 | 130 | 2.5785 | 130 | 3.1877
95 | 0.015625 | 95 | 0.06822 | 97 | 0.14065 | 97 | 0.18418 | 101 | 0.24484 | 101 | 0.30282 | 105 | 0.55454 | 105 | 0.68385 | 111 | 1.2529 | 111 | 1.6208 | 121 | 1.9828 | 121 | 2.391 | 131 | 2.5366 | 131 | 3.1284
96 | 0.015625 | 96 | 0.06671 | 98 | 0.13786 | 98 | 0.18048 | 102 | 0.24093 | 102 | 0.29544 | 106 | 0.54493 | 106 | 0.66846 | 112 | 1.2281 | 112 | 1.5841 | 122 | 1.958 | 122 | 2.358 | 132 | 2.506 | 132 | 3.069
97 | 0.015625 | 97 | 0.06237 | 99 | 0.13507 | 99 | 0.17678 | 103 | 0.23703 | 103 | 0.28805 | 107 | 0.53532 | 107 | 0.65307 | 113 | 1.2033 | 113 | 1.5475 | 123 | 1.9331 | 123 | 2.325 | 133 | 2.4753 | 133 | 3.0097
98 | 0.015625 | 98 | 0.05802 | 100 | 0.13228 | 100 | 0.17308 | 104 | 0.23313 | 104 | 0.28415 | 108 | 0.5257 | 108 | 0.64345 | 114 | 1.1785 | 114 | 1.5108 | 124 | 1.9082 | 124 | 2.2919 | 134 | 2.4447 | 134 | 2.9678
99 | 0.015625 | 99 | 0.05368 | 101 | 0.12949 | 101 | 0.16938 | 105 | 0.22533 | 105 | 0.28025 | 109 | 0.51609 | 109 | 0.63384 | 115 | 1.1289 | 115 | 1.4741 | 125 | 1.8585 | 125 | 2.2589 | 135 | 2.414 | 135 | 2.9259
100 | 0.015625 | 100 | 0.04934 | 102 | 0.12671 | 102 | 0.1666 | 106 | 0.22142 | 106 | 0.27635 | 110 | 0.50647 | 110 | 0.62423 | 116 | 1.1042 | 116 | 1.4374 | 126 | 1.8336 | 126 | 2.2259 | 136 | 2.3527 | 136 | 2.884
101 | 0.015625 | 101 | 0.03334 | 103 | 0.12392 | 103 | 0.16381 | 107 | 0.21752 | 107 | 0.27244 | 111 | 0.49686 | 111 | 0.61461 | 117 | 1.0794 | 117 | 1.4007 | 127 | 1.8087 | 127 | 2.1929 | 137 | 2.322 | 137 | 2.842
453 | 0.015625 | 453 | 0.03334 | 104 | 0.12209 | 104 | 0.16102 | 108 | 0.21362 | 108 | 0.26854 | 112 | 0.48725 | 112 | 0.605 | 118 | 1.0546 | 118 | 1.364 | 128 | 1.7838 | 128 | 2.1599 | 138 | 2.2914 | 138 | 2.8001
454 | 0.011042 | 454 | 0.03334 | 105 | 0.11844 | 105 | 0.15823 | 109 | 0.20972 | 109 | 0.26464 | 113 | 0.47763 | 113 | 0.59538 | 119 | 1.0298 | 119 | 1.3392 | 129 | 1.759 | 129 | 2.1269 | 139 | 2.2607 | 139 | 2.7582
455 | 0.001 | 455 | 0.03334 | 106 | 0.11662 | 106 | 0.15544 | 110 | 0.20582 | 110 | 0.26074 | 114 | 0.46802 | 114 | 0.58577 | 120 | 1.0156 | 120 | 1.3144 | 130 | 1.7341 | 130 | 2.0939 | 140 | 2.23 | 140 | 2.7163
500 | 0.001 | 500 | 0.03334 | 107 | 0.1148 | 107 | 0.15265 | 111 | 0.20191 | 111 | 0.25684 | 115 | 0.45632 | 115 | 0.57616 | 121 | 1.0015 | 121 | 1.2896 | 131 | 1.7092 | 131 | 2.0608 | 141 | 2.1994 | 141 | 2.6744
501 | 0.001 | 501 | 0.01667 | 108 | 0.11297 | 108 | 0.14986 | 112 | 0.19801 | 112 | 0.25293 | 116 | 0.45047 | 116 | 0.56654 | 122 | 0.98731 | 122 | 1.2649 | 132 | 1.6844 | 132 | 2.0278 | 142 | 2.1687 | 142 | 2.6325
6300 | 0.001 | 6300 | 0.01667 | 109 | 0.11115 | 109 | 0.14707 | 113 | 0.19411 | 113 | 0.24903 | 117 | 0.44461 | 117 | 0.55693 | 123 | 0.97314 | 123 | 1.2401 | 133 | 1.6595 | 133 | 1.9948 | 143 | 2.1381 | 143 | 2.5905
|  |  |  | 110 | 0.10932 | 110 | 0.14428 | 114 | 0.19021 | 114 | 0.24513 | 118 | 0.43876 | 118 | 0.54732 | 124 | 0.95897 | 124 | 1.2153 | 134 | 1.6382 | 134 | 1.97 | 144 | 2.1074 | 144 | 2.5486
|  |  |  | 111 | 0.1075 | 111 | 0.14149 | 115 | 0.1824 | 115 | 0.24123 | 119 | 0.43291 | 119 | 0.5377 | 125 | 0.93062 | 125 | 1.1905 | 135 | 1.6169 | 135 | 1.9451 | 145 | 2.0461 | 145 | 2.518
|  |  |  | 112 | 0.10567 | 112 | 0.13871 | 116 | 0.1785 | 116 | 0.23733 | 120 | 0.42706 | 120 | 0.52809 | 126 | 0.91645 | 126 | 1.1657 | 136 | 1.5743 | 136 | 1.9202 | 146 | 2.0154 | 146 | 2.4873
|  |  |  | 113 | 0.10385 | 113 | 0.13592 | 117 | 0.17646 | 117 | 0.23342 | 121 | 0.42121 | 121 | 0.51847 | 127 | 0.90228 | 127 | 1.1409 | 137 | 1.553 | 137 | 1.8953 | 147 | 1.9939 | 147 | 2.4567
|  |  |  | 114 | 0.10203 | 114 | 0.13409 | 118 | 0.17443 | 118 | 0.22952 | 122 | 0.41536 | 122 | 0.50886 | 128 | 0.88811 | 128 | 1.1162 | 138 | 1.5317 | 138 | 1.8705 | 148 | 1.9724 | 148 | 2.426
|  |  |  | 115 | 0.09838 | 115 | 0.13227 | 119 | 0.17239 | 119 | 0.22562 | 123 | 0.40951 | 123 | 0.49925 | 129 | 0.87394 | 129 | 1.0914 | 139 | 1.5105 | 139 | 1.8456 | 149 | 1.9509 | 149 | 2.3954
|  |  |  | 116 | 0.09711 | 116 | 0.13044 | 120 | 0.17035 | 120 | 0.22172 | 124 | 0.40366 | 124 | 0.48963 | 130 | 0.85977 | 130 | 1.0666 | 140 | 1.4892 | 140 | 1.8207 | 150 | 1.9294 | 150 | 2.3647
|  |  |  | 117 | 0.09583 | 117 | 0.12862 | 121 | 0.16832 | 121 | 0.21782 | 125 | 0.39196 | 125 | 0.48002 | 131 | 0.8456 | 131 | 1.0418 | 141 | 1.4679 | 141 | 1.7958 | 151 | 1.9079 | 151 | 2.334
|  |  |  | 118 | 0.09456 | 118 | 0.1268 | 122 | 0.16628 | 122 | 0.21391 | 126 | 0.38611 | 126 | 0.47417 | 132 | 0.83143 | 132 | 1.0276 | 142 | 1.4466 | 142 | 1.771 | 152 | 1.8863 | 152 | 2.3034
|  |  |  | 119 | 0.09329 | 119 | 0.12497 | 123 | 0.16424 | 123 | 0.21001 | 127 | 0.38025 | 127 | 0.46832 | 133 | 0.81726 | 133 | 1.0135 | 143 | 1.4253 | 143 | 1.7461 | 153 | 1.8648 | 153 | 2.2727
|  |  |  | 120 | 0.09201 | 120 | 0.12315 | 124 | 0.1622 | 124 | 0.20611 | 128 | 0.3744 | 128 | 0.46247 | 134 | 0.80309 | 134 | 0.99931 | 144 | 1.404 | 144 | 1.7212 | 154 | 1.8433 | 154 | 2.242
|  |  |  | 121 | 0.09074 | 121 | 0.12132 | 125 | 0.15813 | 125 | 0.20221 | 129 | 0.36855 | 129 | 0.45661 | 135 | 0.78892 | 135 | 0.98514 | 145 | 1.3614 | 145 | 1.6964 | 155 | 1.8218 | 155 | 2.2114
|  |  |  | 122 | 0.08947 | 122 | 0.1195 | 126 | 0.15609 | 126 | 0.19831 | 130 | 0.3627 | 130 | 0.45076 | 136 | 0.7656 | 136 | 0.97097 | 146 | 1.3401 | 146 | 1.6715 | 156 | 1.7788 | 156 | 2.1807
|  |  |  | 123 | 0.0882 | 123 | 0.11767 | 127 | 0.15406 | 127 | 0.1944 | 131 | 0.35685 | 131 | 0.44491 | 137 | 0.75646 | 137 | 0.9568 | 147 | 1.3188 | 147 | 1.6502 | 157 | 1.7572 | 157 | 2.1501
|  |  |  | 124 | 0.08692 | 124 | 0.11585 | 128 | 0.15202 | 128 | 0.1905 | 132 | 0.351 | 132 | 0.43906 | 138 | 0.74731 | 138 | 0.94262 | 148 | 1.3024 | 148 | 1.6289 | 158 | 1.7357 | 158 | 2.1194
|  |  |  | 125 | 0.08438 | 125 | 0.11403 | 129 | 0.14998 | 129 | 0.18846 | 133 | 0.34714 | 133 | 0.43321 | 139 | 0.73817 | 139 | 0.92845 | 149 | 1.286 | 149 | 1.6076 | 159 | 1.7142 | 159 | 2.0888
|  |  |  | 126 | 0.0831 | 126 | 0.1122 | 130 | 0.14794 | 130 | 0.18643 | 134 | 0.34329 | 134 | 0.42736 | 140 | 0.72903 | 140 | 0.91428 | 150 | 1.2696 | 150 | 1.5863 | 160 | 1.6927 | 160 | 2.0581
|  |  |  | 127 | 0.08183 | 127 | 0.11038 | 131 | 0.14591 | 131 | 0.18439 | 135 | 0.33943 | 135 | 0.42151 | 141 | 0.71988 | 141 | 0.90011 | 151 | 1.2532 | 151 | 1.565 | 161 | 1.6712 | 161 | 2.0274
|  |  |  | 128 | 0.08056 | 128 | 0.10911 | 132 | 0.14387 | 132 | 0.18235 | 136 | 0.33172 | 136 | 0.41566 | 142 | 0.71074 | 142 | 0.88594 | 152 | 1.2368 | 152 | 1.5437 | 162 | 1.6497 | 162 | 2.0059
|  |  |  | 129 | 0.07929 | 129 | 0.10783 | 133 | 0.14183 | 133 | 0.18032 | 137 | 0.32786 | 137 | 0.40981 | 143 | 0.7016 | 143 | 0.87177 | 153 | 1.2203 | 153 | 1.5225 | 163 | 1.6282 | 163 | 1.9844
|  |  |  | 130 | 0.07801 | 130 | 0.10656 | 134 | 0.1398 | 134 | 0.17828 | 138 | 0.32401 | 138 | 0.40396 | 144 | 0.69245 | 144 | 0.8576 | 154 | 1.2039 | 154 | 1.5012 | 164 | 1.6066 | 164 | 1.9629
|  |  |  | 131 | 0.07674 | 131 | 0.10529 | 135 | 0.13776 | 135 | 0.17624 | 139 | 0.32015 | 139 | 0.39811 | 145 | 0.67416 | 145 | 0.84343 | 155 | 1.1875 | 155 | 1.4799 | 165 | 1.5636 | 165 | 1.9414
|  |  |  | 132 | 0.06945 | 132 | 0.10401 | 136 | 0.13368 | 136 | 0.1742 | 140 | 0.3163 | 140 | 0.39225 | 146 | 0.66502 | 146 | 0.82926 | 156 | 1.1547 | 156 | 1.4586 | 166 | 1.5421 | 166 | 1.9199
|  |  |  | 133 | 0.06216 | 133 | 0.10274 | 137 | 0.13165 | 137 | 0.17217 | 141 | 0.31244 | 141 | 0.3864 | 147 | 0.65588 | 147 | 0.81509 | 157 | 1.1383 | 157 | 1.4373 | 167 | 1.5206 | 167 | 1.8983
|  |  |  | 134 | 0.05487 | 134 | 0.10147 | 138 | 0.12961 | 138 | 0.17013 | 142 | 0.30858 | 142 | 0.38055 | 148 | 0.64673 | 148 | 0.80092 | 158 | 1.1219 | 158 | 1.416 | 168 | 1.4991 | 168 | 1.8768
|  |  |  | 135 | 0.04758 | 135 | 0.1002 | 139 | 0.12757 | 139 | 0.16809 | 143 | 0.30473 | 143 | 0.3747 | 149 | 0.63759 | 149 | 0.78675 | 159 | 1.1054 | 159 | 1.3947 | 169 | 1.4836 | 169 | 1.8553
|  |  |  | 136 | 0.015625 | 136 | 0.09892 | 140 | 0.12554 | 140 | 0.16606 | 144 | 0.30087 | 144 | 0.36885 | 150 | 0.62845 | 150 | 0.7776 | 160 | 1.089 | 160 | 1.3734 | 170 | 1.4681 | 170 | 1.8338
|  |  |  | 137 | 0.015625 | 137 | 0.09765 | 141 | 0.1235 | 141 | 0.16402 | 145 | 0.29316 | 145 | 0.363 | 151 | 0.6193 | 151 | 0.76846 | 161 | 1.0764 | 161 | 1.3521 | 171 | 1.4527 | 171 | 1.8123
|  |  |  | 138 | 0.015625 | 138 | 0.09638 | 142 | 0.12146 | 142 | 0.16198 | 146 | 0.2893 | 146 | 0.35914 | 152 | 0.61016 | 152 | 0.75931 | 162 | 1.0639 | 162 | 1.3308 | 172 | 1.4372 | 172 | 1.7908
|  |  |  | 139 | 0.015625 | 139 | 0.0951 | 143 | 0.12037 | 143 | 0.15994 | 147 | 0.28545 | 147 | 0.35529 | 153 | 0.60101 | 153 | 0.75017 | 163 | 1.0513 | 163 | 1.3144 | 173 | 1.4217 | 173 | 1.7692
|  |  |  | 140 | 0.015625 | 140 | 0.09383 | 144 | 0.11928 | 144 | 0.15791 | 148 | 0.28159 | 148 | 0.35143 | 154 | 0.59187 | 154 | 0.74103 | 164 | 1.0388 | 164 | 1.298 | 174 | 1.4063 | 174 | 1.7477
|  |  |  | 141 | 0.015625 | 141 | 0.09256 | 145 | 0.11709 | 145 | 0.15587 | 149 | 0.27773 | 149 | 0.34758 | 155 | 0.58273 | 155 | 0.73188 | 165 | 1.0136 | 165 | 1.2816 | 175 | 1.3753 | 175 | 1.7262
|  |  |  | 142 | 0.015625 | 142 | 0.09129 | 146 | 0.116 | 146 | 0.15383 | 150 | 0.27388 | 150 | 0.34372 | 156 | 0.56444 | 156 | 0.72274 | 166 | 1.0011 | 166 | 1.2652 | 176 | 1.3599 | 176 | 1.7047
|  |  |  | 143 | 0.015625 | 143 | 0.09001 | 147 | 0.11491 | 147 | 0.1518 | 151 | 0.27002 | 151 | 0.33986 | 157 | 0.55904 | 157 | 0.7136 | 167 | 0.98849 | 167 | 1.2488 | 177 | 1.3444 | 177 | 1.6832
|  |  |  | 144 | 0.015625 | 144 | 0.08874 | 148 | 0.11382 | 148 | 0.14976 | 152 | 0.26617 | 152 | 0.33601 | 158 | 0.55364 | 158 | 0.70445 | 168 | 0.97593 | 168 | 1.2323 | 178 | 1.329 | 178 | 1.6617
|  |  |  | 145 | 0.015625 | 145 | 0.08145 | 149 | 0.11273 | 149 | 0.14772 | 153 | 0.26231 | 153 | 0.33215 | 159 | 0.54825 | 159 | 0.69531 | 169 | 0.96336 | 169 | 1.2159 | 179 | 1.3135 | 179 | 1.6402
|  |  |  | 146 | 0.015625 | 146 | 0.07416 | 150 | 0.11164 | 150 | 0.14568 | 154 | 0.25845 | 154 | 0.3283 | 160 | 0.54285 | 160 | 0.68616 | 170 | 0.95079 | 170 | 1.1995 | 180 | 1.298 | 180 | 1.6186
|  |  |  | 147 | 0.015625 | 147 | 0.06687 | 151 | 0.11054 | 151 | 0.14365 | 155 | 0.2546 | 155 | 0.32444 | 161 | 0.53745 | 161 | 0.67702 | 171 | 0.93823 | 171 | 1.1831 | 181 | 1.287 | 181 | 1.5971
|  |  |  | 148 | 0.015625 | 148 | 0.05958 | 152 | 0.10945 | 152 | 0.14161 | 156 | 0.24853 | 156 | 0.32058 | 162 | 0.53205 | 162 | 0.66788 | 172 | 0.92566 | 172 | 1.1667 | 182 | 1.276 | 182 | 1.5756
|  |  |  | 149 | 0.015625 | 149 | 0.05229 | 153 | 0.10836 | 153 | 0.13957 | 157 | 0.24631 | 157 | 0.31673 | 163 | 0.52665 | 163 | 0.65873 | 173 | 0.9131 | 173 | 1.1503 | 183 | 1.265 | 183 | 1.5541
|  |  |  | 150 | 0.015625 | 150 | 0.03334 | 154 | 0.10727 | 154 | 0.13754 | 158 | 0.2441 | 158 | 0.31287 | 164 | 0.52126 | 164 | 0.64959 | 174 | 0.90053 | 174 | 1.1339 | 184 | 1.254 | 184 | 1.5326
|  |  |  | 453 | 0.015625 | 453 | 0.03334 | 155 | 0.10618 | 155 | 0.1355 | 159 | 0.24188 | 159 | 0.30901 | 165 | 0.51046 | 165 | 0.64045 | 175 | 0.8754 | 175 | 1.1174 | 185 | 1.232 | 185 | 1.5111
|  |  |  | 454 | 0.011042 | 454 | 0.03334 | 156 | 0.10399 | 156 | 0.13346 | 160 | 0.23967 | 160 | 0.30516 | 166 | 0.50506 | 166 | 0.6313 | 176 | 0.86283 | 176 | 1.101 | 186 | 1.221 | 186 | 1.4956
|  |  |  | 455 | 0.001 | 455 | 0.03334 | 157 | 0.1029 | 157 | 0.13237 | 161 | 0.23745 | 161 | 0.3013 | 167 | 0.49967 | 167 | 0.62216 | 177 | 0.85027 | 177 | 1.0884 | 187 | 1.21 | 187 | 1.4801
|  |  |  | 500 | 0.001 | 500 | 0.03334 | 158 | 0.10181 | 158 | 0.13128 | 162 | 0.23524 | 162 | 0.29745 | 168 | 0.49427 | 168 | 0.61301 | 178 | 0.8377 | 178 | 1.0759 | 188 | 1.199 | 188 | 1.4647
|  |  |  | 501 | 0.001 | 501 | 0.01667 | 159 | 0.10072 | 159 | 0.13019 | 163 | 0.23302 | 163 | 0.29359 | 169 | 0.48887 | 169 | 0.60387 | 179 | 0.82514 | 179 | 1.0633 | 189 | 1.188 | 189 | 1.4492
|  |  |  | 6300 | 0.001 | 6300 | 0.01667 | 160 | 0.09963 | 160 | 0.12909 | 164 | 0.23081 | 164 | 0.28973 | 170 | 0.48347 | 170 | 0.59473 | 180 | 0.81257 | 180 | 1.0508 | 190 | 1.1769 | 190 | 1.4337
[8 empty] | 161 | 0.09854 | 161 | 0.128 | 165 | 0.22638 | 165 | 0.28588 | 171 | 0.47807 | 171 | 0.58558 | 181 | 0.8 | 181 | 1.0382 | 191 | 1.1659 | 191 | 1.4183
[8 empty] | 162 | 0.09744 | 162 | 0.12691 | 166 | 0.22416 | 166 | 0.28202 | 172 | 0.47268 | 172 | 0.57644 | 182 | 0.79253 | 182 | 1.0256 | 192 | 1.1549 | 192 | 1.4028
[8 empty] | 163 | 0.09635 | 163 | 0.12582 | 167 | 0.22195 | 167 | 0.27817 | 173 | 0.46728 | 173 | 0.57104 | 183 | 0.78506 | 183 | 1.0131 | 193 | 1.1439 | 193 | 1.3873
[8 empty] | 164 | 0.09526 | 164 | 0.12473 | 168 | 0.21973 | 168 | 0.27431 | 174 | 0.46188 | 174 | 0.56564 | 184 | 0.77758 | 184 | 1.0005 | 194 | 1.1329 | 194 | 1.3719
[8 empty] | 165 | 0.09308 | 165 | 0.12364 | 169 | 0.21752 | 169 | 0.27045 | 175 | 0.45108 | 175 | 0.56025 | 185 | 0.76264 | 185 | 0.98793 | 195 | 1.1109 | 195 | 1.3564
[8 empty] | 166 | 0.09199 | 166 | 0.12254 | 170 | 0.2153 | 170 | 0.2666 | 176 | 0.44569 | 176 | 0.55485 | 186 | 0.75516 | 186 | 0.97536 | 196 | 1.0999 | 196 | 1.341
[8 empty] | 167 | 0.09089 | 167 | 0.12145 | 171 | 0.21309 | 171 | 0.26274 | 177 | 0.44029 | 177 | 0.54945 | 187 | 0.74769 | 187 | 0.96279 | 197 | 1.0889 | 197 | 1.3255
[8 empty] | 168 | 0.0898 | 168 | 0.12036 | 172 | 0.21087 | 172 | 0.26053 | 178 | 0.43489 | 178 | 0.54405 | 188 | 0.74022 | 188 | 0.95023 | 198 | 1.0779 | 198 | 1.31
[8 empty] | 169 | 0.08871 | 169 | 0.11927 | 173 | 0.20866 | 173 | 0.25831 | 179 | 0.42949 | 179 | 0.53865 | 189 | 0.73274 | 189 | 0.93766 | 199 | 1.0669 | 199 | 1.299
[8 empty] | 170 | 0.08762 | 170 | 0.11818 | 174 | 0.20644 | 174 | 0.2561 | 180 | 0.42608 | 180 | 0.53326 | 190 | 0.72527 | 190 | 0.9251 | 200 | 1.0559 | 200 | 1.288
[8 empty] | 171 | 0.08653 | 171 | 0.11709 | 175 | 0.20201 | 175 | 0.25388 | 181 | 0.42267 | 181 | 0.52786 | 191 | 0.7178 | 191 | 0.91253 | 201 | 1.0449 | 201 | 1.277
[8 empty] | 172 | 0.08544 | 172 | 0.11599 | 176 | 0.19979 | 176 | 0.25167 | 182 | 0.41926 | 182 | 0.52246 | 192 | 0.71032 | 192 | 0.89997 | 202 | 1.0339 | 202 | 1.266
[8 empty] | 173 | 0.08434 | 173 | 0.1149 | 177 | 0.19758 | 177 | 0.24945 | 183 | 0.41585 | 183 | 0.51706 | 193 | 0.70285 | 193 | 0.8874 | 203 | 1.0229 | 203 | 1.255
[8 empty] | 174 | 0.08325 | 174 | 0.11381 | 178 | 0.19536 | 178 | 0.24724 | 184 | 0.41244 | 184 | 0.51167 | 194 | 0.69538 | 194 | 0.87483 | 204 | 1.0118 | 204 | 1.244
[8 empty] | 175 | 0.08107 | 175 | 0.11272 | 179 | 0.19315 | 179 | 0.24502 | 185 | 0.40562 | 185 | 0.50627 | 195 | 0.68043 | 195 | 0.86227 | 205 | 0.99294 | 205 | 1.233
[8 empty] | 176 | 0.07998 | 176 | 0.11163 | 180 | 0.19093 | 180 | 0.24281 | 186 | 0.40221 | 186 | 0.50087 | 196 | 0.67295 | 196 | 0.8497 | 206 | 0.98504 | 206 | 1.222
[8 empty] | 177 | 0.07889 | 177 | 0.11054 | 181 | 0.18872 | 181 | 0.24059 | 187 | 0.3988 | 187 | 0.49547 | 197 | 0.66548 | 197 | 0.83714 | 207 | 0.97714 | 207 | 1.211
[8 empty] | 178 | 0.07779 | 178 | 0.10944 | 182 | 0.1865 | 182 | 0.23838 | 188 | 0.39539 | 188 | 0.49007 | 198 | 0.65801 | 198 | 0.82457 | 208 | 0.96924 | 208 | 1.2
[8 empty] | 179 | 0.0767 | 179 | 0.10835 | 183 | 0.18429 | 183 | 0.23616 | 189 | 0.39198 | 189 | 0.48468 | 199 | 0.65053 | 199 | 0.812 | 209 | 0.96135 | 209 | 1.1889
[8 empty] | 180 | 0.07561 | 180 | 0.10726 | 184 | 0.18207 | 184 | 0.23395 | 190 | 0.38857 | 190 | 0.47928 | 200 | 0.64306 | 200 | 0.80453 | 210 | 0.95345 | 210 | 1.1779
[8 empty] | 181 | 0.07508 | 181 | 0.10617 | 185 | 0.17764 | 185 | 0.23173 | 191 | 0.38516 | 191 | 0.47388 | 201 | 0.63753 | 201 | 0.79706 | 211 | 0.94555 | 211 | 1.1669
[8 empty] | 182 | 0.07455 | 182 | 0.10508 | 186 | 0.17623 | 186 | 0.22952 | 192 | 0.38175 | 192 | 0.46848 | 202 | 0.632 | 202 | 0.78958 | 212 | 0.93765 | 212 | 1.1559
[8 empty] | 183 | 0.07401 | 183 | 0.10399 | 187 | 0.17481 | 187 | 0.2273 | 193 | 0.37834 | 193 | 0.46308 | 203 | 0.62646 | 203 | 0.78211 | 213 | 0.92975 | 213 | 1.1449
[8 empty] | 184 | 0.07348 | 184 | 0.10289 | 188 | 0.1734 | 188 | 0.22509 | 194 | 0.37493 | 194 | 0.45769 | 204 | 0.62093 | 204 | 0.77464 | 214 | 0.92185 | 214 | 1.1339
[8 empty] | 185 | 0.07242 | 185 | 0.1018 | 189 | 0.17198 | 189 | 0.22287 | 195 | 0.36811 | 195 | 0.45229 | 205 | 0.60987 | 205 | 0.76716 | 215 | 0.90605 | 215 | 1.1229
[8 empty] | 186 | 0.07188 | 186 | 0.10071 | 190 | 0.17057 | 190 | 0.22066 | 196 | 0.3647 | 196 | 0.44689 | 206 | 0.60433 | 206 | 0.75969 | 216 | 0.89815 | 216 | 1.1119
[8 empty] | 187 | 0.07135 | 187 | 0.09962 | 191 | 0.16915 | 191 | 0.21844 | 197 | 0.36129 | 197 | 0.44149 | 207 | 0.5988 | 207 | 0.75222 | 217 | 0.89025 | 217 | 1.1009
[8 empty] | 188 | 0.07082 | 188 | 0.09853 | 192 | 0.16774 | 192 | 0.21623 | 198 | 0.35788 | 198 | 0.43808 | 208 | 0.59327 | 208 | 0.74474 | 218 | 0.88236 | 218 | 1.0899
[8 empty] | 189 | 0.07029 | 189 | 0.09744 | 193 | 0.16632 | 193 | 0.21401 | 199 | 0.35447 | 199 | 0.43467 | 209 | 0.58774 | 209 | 0.73727 | 219 | 0.87446 | 219 | 1.0789
[8 empty] | 190 | 0.06975 | 190 | 0.09634 | 194 | 0.16491 | 194 | 0.21179 | 200 | 0.35106 | 200 | 0.43126 | 210 | 0.5822 | 210 | 0.7298 | 220 | 0.86656 | 220 | 1.0679
[8 empty] | 191 | 0.06922 | 191 | 0.09525 | 195 | 0.16208 | 195 | 0.20958 | 201 | 0.34765 | 201 | 0.42785 | 211 | 0.57667 | 211 | 0.72232 | 221 | 0.85866 | 221 | 1.0569
[8 empty] | 192 | 0.06869 | 192 | 0.09416 | 196 | 0.16066 | 196 | 0.20736 | 202 | 0.34424 | 202 | 0.42444 | 212 | 0.57114 | 212 | 0.71485 | 222 | 0.85076 | 222 | 1.0459
[8 empty] | 193 | 0.06816 | 193 | 0.09307 | 197 | 0.15925 | 197 | 0.20515 | 203 | 0.34083 | 203 | 0.42103 | 213 | 0.56561 | 213 | 0.70738 | 223 | 0.84286 | 223 | 1.0349
[8 empty] | 194 | 0.06762 | 194 | 0.09198 | 198 | 0.15783 | 198 | 0.20293 | 204 | 0.33742 | 204 | 0.41762 | 214 | 0.56007 | 214 | 0.6999 | 224 | 0.83496 | 224 | 1.0238
[8 empty] | 195 | 0.06656 | 195 | 0.09089 | 199 | 0.15642 | 199 | 0.20072 | 205 | 0.3306 | 205 | 0.41421 | 215 | 0.54901 | 215 | 0.69243 | 225 | 0.81916 | 225 | 1.0128
[8 empty] | 196 | 0.06603 | 196 | 0.08979 | 200 | 0.15501 | 200 | 0.1985 | 206 | 0.32719 | 206 | 0.4108 | 216 | 0.54348 | 216 | 0.68495 | 226 | 0.81127 | 226 | 1.0049
[8 empty] | 197 | 0.06549 | 197 | 0.0887 | 201 | 0.15359 | 201 | 0.19629 | 207 | 0.32378 | 207 | 0.40739 | 217 | 0.53794 | 217 | 0.67748 | 227 | 0.80503 | 227 | 0.99704
[8 empty] | 198 | 0.06496 | 198 | 0.08761 | 202 | 0.15218 | 202 | 0.19407 | 208 | 0.32037 | 208 | 0.40398 | 218 | 0.53241 | 218 | 0.67001 | 228 | 0.79879 | 228 | 0.98914
[8 empty] | 199 | 0.06443 | 199 | 0.08708 | 203 | 0.15076 | 203 | 0.19186 | 209 | 0.31696 | 209 | 0.40057 | 219 | 0.52688 | 219 | 0.66253 | 229 | 0.79255 | 229 | 0.98124
[8 empty] | 200 | 0.0639 | 200 | 0.08655 | 204 | 0.14935 | 204 | 0.18964 | 210 | 0.31356 | 210 | 0.39716 | 220 | 0.52135 | 220 | 0.65506 | 230 | 0.78631 | 230 | 0.97335
[8 empty] | 201 | 0.06336 | 201 | 0.08601 | 205 | 0.14652 | 205 | 0.18823 | 211 | 0.31132 | 211 | 0.39375 | 221 | 0.51581 | 221 | 0.64953 | 231 | 0.78007 | 231 | 0.96545
[8 empty] | 202 | 0.06283 | 202 | 0.08548 | 206 | 0.1451 | 206 | 0.18681 | 212 | 0.30909 | 212 | 0.39034 | 222 | 0.51028 | 222 | 0.644 | 232 | 0.77383 | 232 | 0.95755
[8 empty] | 203 | 0.0623 | 203 | 0.08495 | 207 | 0.14369 | 207 | 0.1854 | 213 | 0.30685 | 213 | 0.38693 | 223 | 0.50475 | 223 | 0.63846 | 233 | 0.76759 | 233 | 0.94965
[8 empty] | 204 | 0.06177 | 204 | 0.08442 | 208 | 0.14227 | 208 | 0.18398 | 214 | 0.30462 | 214 | 0.38352 | 224 | 0.50122 | 224 | 0.63293 | 234 | 0.76135 | 234 | 0.94175
[8 empty] | 205 | 0.0607 | 205 | 0.08388 | 209 | 0.14086 | 209 | 0.18257 | 215 | 0.30015 | 215 | 0.38011 | 225 | 0.49417 | 225 | 0.6274 | 235 | 0.75511 | 235 | 0.93385
[8 empty] | 206 | 0.06017 | 206 | 0.08335 | 210 | 0.13944 | 210 | 0.18115 | 216 | 0.29792 | 216 | 0.3767 | 226 | 0.49064 | 226 | 0.62187 | 236 | 0.74263 | 236 | 0.92595
[8 empty] | 207 | 0.05964 | 207 | 0.08282 | 211 | 0.13803 | 211 | 0.17974 | 217 | 0.29568 | 217 | 0.37329 | 227 | 0.48711 | 227 | 0.61633 | 237 | 0.7364 | 237 | 0.91805
[8 empty] | 208 | 0.0591 | 208 | 0.08229 | 212 | 0.13661 | 212 | 0.17832 | 218 | 0.29345 | 218 | 0.36988 | 228 | 0.48359 | 228 | 0.6108 | 238 | 0.73016 | 238 | 0.91015
[8 empty] | 209 | 0.05857 | 209 | 0.08175 | 213 | 0.1352 | 213 | 0.17691 | 219 | 0.29122 | 219 | 0.36647 | 229 | 0.48006 | 229 | 0.60527 | 239 | 0.72392 | 239 | 0.90225
[8 empty] | 210 | 0.05804 | 210 | 0.08122 | 214 | 0.13378 | 214 | 0.17549 | 220 | 0.28898 | 220 | 0.36306 | 230 | 0.47653 | 230 | 0.59974 | 240 | 0.71768 | 240 | 0.89436
[8 empty] | 211 | 0.05751 | 211 | 0.08069 | 215 | 0.13198 | 215 | 0.17408 | 221 | 0.28675 | 221 | 0.35965 | 231 | 0.47301 | 231 | 0.5942 | 241 | 0.71144 | 241 | 0.88646
[8 empty] | 212 | 0.05697 | 212 | 0.08016 | 216 | 0.13108 | 216 | 0.17266 | 222 | 0.28452 | 222 | 0.35624 | 232 | 0.46948 | 232 | 0.58867 | 242 | 0.7052 | 242 | 0.87856
[8 empty] | 213 | 0.05644 | 213 | 0.07962 | 217 | 0.13018 | 217 | 0.17125 | 223 | 0.28228 | 223 | 0.35283 | 233 | 0.46595 | 233 | 0.58314 | 243 | 0.69896 | 243 | 0.87066
[8 empty] | 214 | 0.05591 | 214 | 0.07909 | 218 | 0.12928 | 218 | 0.16983 | 224 | 0.28005 | 224 | 0.34942 | 234 | 0.46243 | 234 | 0.57761 | 244 | 0.69418 | 244 | 0.86276
[8 empty] | 215 | 0.05484 | 215 | 0.07856 | 219 | 0.12839 | 219 | 0.16842 | 225 | 0.27558 | 225 | 0.34601 | 235 | 0.4589 | 235 | 0.57207 | 245 | 0.68463 | 245 | 0.85486
[8 empty] | 216 | 0.05431 | 216 | 0.07803 | 220 | 0.12749 | 220 | 0.16701 | 226 | 0.27335 | 226 | 0.3426 | 236 | 0.45185 | 236 | 0.56654 | 246 | 0.67985 | 246 | 0.84696
[8 empty] | 217 | 0.05378 | 217 | 0.07749 | 221 | 0.12659 | 221 | 0.16559 | 227 | 0.27111 | 227 | 0.33919 | 237 | 0.44832 | 237 | 0.56101 | 247 | 0.67507 | 247 | 0.83906
[8 empty] | 218 | 0.05325 | 218 | 0.07696 | 222 | 0.12569 | 222 | 0.16418 | 228 | 0.26888 | 228 | 0.33578 | 238 | 0.44479 | 238 | 0.55548 | 248 | 0.67029 | 248 | 0.83116
[8 empty] | 219 | 0.05271 | 219 | 0.07643 | 223 | 0.12479 | 223 | 0.16276 | 229 | 0.26664 | 229 | 0.33237 | 239 | 0.44127 | 239 | 0.54994 | 249 | 0.66551 | 249 | 0.82327
[8 empty] | 220 | 0.05218 | 220 | 0.0759 | 224 | 0.12389 | 224 | 0.16135 | 230 | 0.26441 | 230 | 0.32896 | 240 | 0.43774 | 240 | 0.54441 | 250 | 0.66073 | 250 | 0.81703
[8 empty] | 221 | 0.05165 | 221 | 0.07536 | 225 | 0.12209 | 225 | 0.15993 | 231 | 0.26218 | 231 | 0.32556 | 241 | 0.43421 | 241 | 0.53888 | 251 | 0.65595 | 251 | 0.81079
[8 empty] | 222 | 0.05112 | 222 | 0.07483 | 226 | 0.12119 | 226 | 0.15852 | 232 | 0.25994 | 232 | 0.32332 | 242 | 0.43068 | 242 | 0.53335 | 252 | 0.65117 | 252 | 0.80455
[8 empty] | 223 | 0.05058 | 223 | 0.0743 | 227 | 0.12029 | 227 | 0.1571 | 233 | 0.25771 | 233 | 0.32109 | 243 | 0.42716 | 243 | 0.52781 | 253 | 0.6464 | 253 | 0.79831
[8 empty] | 224 | 0.05005 | 224 | 0.07377 | 228 | 0.11939 | 228 | 0.15569 | 234 | 0.25548 | 234 | 0.31885 | 244 | 0.42363 | 244 | 0.52228 | 254 | 0.64162 | 254 | 0.79207
[8 empty] | 225 | 0.04899 | 225 | 0.07323 | 229 | 0.11849 | 229 | 0.15427 | 235 | 0.25324 | 235 | 0.31662 | 245 | 0.41658 | 245 | 0.51675 | 255 | 0.63684 | 255 | 0.78583
[8 empty] | 226 | 0.04845 | 226 | 0.0727 | 230 | 0.11759 | 230 | 0.15286 | 236 | 0.24877 | 236 | 0.31439 | 246 | 0.41305 | 246 | 0.51322 | 256 | 0.62728 | 256 | 0.77959
[8 empty] | 227 | 0.015625 | 227 | 0.07217 | 231 | 0.11669 | 231 | 0.15144 | 237 | 0.24654 | 237 | 0.31215 | 247 | 0.40952 | 247 | 0.50969 | 257 | 0.6225 | 257 | 0.77335
[8 empty] | 228 | 0.015625 | 228 | 0.07164 | 232 | 0.11579 | 232 | 0.15003 | 238 | 0.24431 | 238 | 0.30992 | 248 | 0.40696 | 248 | 0.50617 | 258 | 0.61772 | 258 | 0.76711
[8 empty] | 229 | 0.015625 | 229 | 0.0711 | 233 | 0.1149 | 233 | 0.14861 | 239 | 0.24207 | 239 | 0.30768 | 249 | 0.40439 | 249 | 0.50264 | 259 | 0.61295 | 259 | 0.76087
[8 empty] | 230 | 0.015625 | 230 | 0.07057 | 234 | 0.114 | 234 | 0.1472 | 240 | 0.24063 | 240 | 0.30545 | 250 | 0.40182 | 250 | 0.49911 | 260 | 0.60817 | 260 | 0.75463
[8 empty] | 231 | 0.015625 | 231 | 0.07004 | 235 | 0.1131 | 235 | 0.14578 | 241 | 0.2392 | 241 | 0.30322 | 251 | 0.39925 | 251 | 0.49559 | 261 | 0.60339 | 261 | 0.7484
[8 empty] | 232 | 0.015625 | 232 | 0.06951 | 236 | 0.1113 | 236 | 0.14488 | 242 | 0.23776 | 242 | 0.30098 | 252 | 0.39668 | 252 | 0.49206 | 262 | 0.59861 | 262 | 0.74216
[8 empty] | 233 | 0.015625 | 233 | 0.06897 | 237 | 0.1104 | 237 | 0.14398 | 243 | 0.23632 | 243 | 0.29875 | 253 | 0.39412 | 253 | 0.48853 | 263 | 0.59383 | 263 | 0.73592
[8 empty] | 234 | 0.015625 | 234 | 0.06844 | 238 | 0.1095 | 238 | 0.14308 | 244 | 0.23488 | 244 | 0.29652 | 254 | 0.39155 | 254 | 0.48501 | 264 | 0.59197 | 264 | 0.72968
[8 empty] | 235 | 0.015625 | 235 | 0.06791 | 239 | 0.1086 | 239 | 0.14218 | 245 | 0.23201 | 245 | 0.29428 | 255 | 0.38898 | 255 | 0.48148 | 265 | 0.58825 | 265 | 0.72344
[8 empty] | 236 | 0.015625 | 236 | 0.06738 | 240 | 0.1077 | 240 | 0.14128 | 246 | 0.23057 | 246 | 0.29205 | 256 | 0.38384 | 256 | 0.47795 | 266 | 0.5864 | 266 | 0.7172
[8 empty] | 237 | 0.015625 | 237 | 0.06684 | 241 | 0.1068 | 241 | 0.14039 | 247 | 0.22913 | 247 | 0.28981 | 257 | 0.38128 | 257 | 0.47443 | 267 | 0.58454 | 267 | 0.71096
[8 empty] | 238 | 0.015625 | 238 | 0.06631 | 242 | 0.1059 | 242 | 0.13949 | 248 | 0.22769 | 248 | 0.28758 | 258 | 0.37871 | 258 | 0.4709 | 268 | 0.58268 | 268 | 0.70618
[8 empty] | 239 | 0.015625 | 239 | 0.06578 | 243 | 0.105 | 243 | 0.13859 | 249 | 0.22625 | 249 | 0.28535 | 259 | 0.37614 | 259 | 0.46737 | 269 | 0.58082 | 269 | 0.7014
[8 empty] | 240 | 0.015625 | 240 | 0.06525 | 244 | 0.1041 | 244 | 0.13769 | 250 | 0.22482 | 250 | 0.28311 | 260 | 0.37357 | 260 | 0.46385 | 270 | 0.57896 | 270 | 0.69663
[8 empty] | 241 | 0.015625 | 241 | 0.06471 | 245 | 0.1023 | 245 | 0.13679 | 251 | 0.22338 | 251 | 0.28088 | 261 | 0.371 | 261 | 0.46032 | 271 | 0.5771 | 271 | 0.69185
[8 empty] | 242 | 0.015625 | 242 | 0.06418 | 246 | 0.10141 | 246 | 0.13589 | 252 | 0.22194 | 252 | 0.27864 | 262 | 0.36843 | 262 | 0.45679 | 272 | 0.55851 | 272 | 0.68707
[8 empty] | 243 | 0.015625 | 243 | 0.06365 | 247 | 0.10051 | 247 | 0.13499 | 253 | 0.2205 | 253 | 0.27641 | 263 | 0.36587 | 263 | 0.45327 | 273 | 0.015625 | 273 | 0.68229
[8 empty] | 244 | 0.015625 | 244 | 0.06312 | 248 | 0.09961 | 248 | 0.13409 | 254 | 0.21906 | 254 | 0.27418 | 264 | 0.3633 | 264 | 0.44974 | 274 | 0.015625 | 274 | 0.67751
[8 empty] | 245 | 0.015625 | 245 | 0.06258 | 249 | 0.099 | 249 | 0.13319 | 255 | 0.21763 | 255 | 0.27194 | 265 | 0.35816 | 265 | 0.44621 | 275 | 0.015625 | 275 | 0.67273
[8 empty] | 246 | 0.015625 | 246 | 0.06205 | 250 | 0.0984 | 250 | 0.13229 | 256 | 0.21475 | 256 | 0.26971 | 266 | 0.35559 | 266 | 0.44268 | 276 | 0.015625 | 276 | 0.66795
[8 empty] | 247 | 0.015625 | 247 | 0.06152 | 251 | 0.0978 | 251 | 0.13139 | 257 | 0.21331 | 257 | 0.26748 | 267 | 0.35303 | 267 | 0.43916 | 277 | 0.015625 | 277 | 0.66317
[8 empty] | 248 | 0.015625 | 248 | 0.06099 | 252 | 0.0972 | 252 | 0.13049 | 258 | 0.21187 | 258 | 0.26524 | 268 | 0.35046 | 268 | 0.43563 | 278 | 0.015625 | 278 | 0.6584
[8 empty] | 249 | 0.015625 | 249 | 0.06045 | 253 | 0.09659 | 253 | 0.12959 | 259 | 0.21044 | 259 | 0.26301 | 269 | 0.34789 | 269 | 0.4321 | 279 | 0.015625 | 279 | 0.65362
[8 empty] | 250 | 0.015625 | 250 | 0.03334 | 254 | 0.09599 | 254 | 0.12869 | 260 | 0.209 | 260 | 0.26077 | 270 | 0.34532 | 270 | 0.42858 | 280 | 0.015625 | 280 | 0.64884
[8 empty] | 453 | 0.015625 | 453 | 0.03334 | 255 | 0.09539 | 255 | 0.12779 | 261 | 0.20756 | 261 | 0.25854 | 271 | 0.34275 | 271 | 0.42505 | 281 | 0.015625 | 281 | 0.64406
[8 empty] | 454 | 0.011042 | 454 | 0.03334 | 256 | 0.09418 | 256 | 0.1269 | 262 | 0.20612 | 262 | 0.25631 | 272 | 0.34019 | 272 | 0.42152 | 282 | 0.015625 | 282 | 0.63928
[8 empty] | 455 | 0.001 | 455 | 0.03334 | 257 | 0.09358 | 257 | 0.126 | 263 | 0.20468 | 263 | 0.25407 | 273 | 0.33762 | 273 | 0.41896 | 283 | 0.015625 | 283 | 0.6345
[8 empty] | 500 | 0.001 | 500 | 0.03334 | 258 | 0.09298 | 258 | 0.1251 | 264 | 0.20325 | 264 | 0.25263 | 274 | 0.33505 | 274 | 0.41639 | 284 | 0.015625 | 284 | 0.62972
[8 empty] | 501 | 0.001 | 501 | 0.01667 | 259 | 0.09238 | 259 | 0.1242 | 265 | 0.20037 | 265 | 0.2512 | 275 | 0.33248 | 275 | 0.41382 | 285 | 0.015625 | 285 | 0.62495
[8 empty] | 6300 | 0.001 | 6300 | 0.01667 | 260 | 0.09177 | 260 | 0.1233 | 266 | 0.19893 | 266 | 0.24976 | 276 | 0.32735 | 276 | 0.41125 | 286 | 0.015625 | 286 | 0.62017
[12 empty] | 261 | 0.09117 | 261 | 0.1224 | 267 | 0.19749 | 267 | 0.24832 | 277 | 0.32478 | 277 | 0.40868 | 287 | 0.015625 | 287 | 0.61539
[12 empty] | 262 | 0.09057 | 262 | 0.1215 | 268 | 0.19606 | 268 | 0.24688 | 278 | 0.32221 | 278 | 0.40612 | 288 | 0.015625 | 288 | 0.61061
[12 empty] | 263 | 0.08997 | 263 | 0.1206 | 269 | 0.19462 | 269 | 0.24544 | 279 | 0.31964 | 279 | 0.40355 | 289 | 0.015625 | 289 | 0.60583
[12 empty] | 264 | 0.08936 | 264 | 0.1197 | 270 | 0.19318 | 270 | 0.24401 | 280 | 0.31707 | 280 | 0.40098 | 290 | 0.015625 | 290 | 0.60397
[12 empty] | 265 | 0.08816 | 265 | 0.1188 | 271 | 0.19174 | 271 | 0.24257 | 281 | 0.31451 | 281 | 0.39841 | 291 | 0.015625 | 291 | 0.60211
[12 empty] | 266 | 0.08756 | 266 | 0.1179 | 272 | 0.1903 | 272 | 0.24113 | 282 | 0.31194 | 282 | 0.39584 | 292 | 0.015625 | 292 | 0.60025
[12 empty] | 267 | 0.08695 | 267 | 0.117 | 273 | 0.015625 | 273 | 0.23969 | 283 | 0.015625 | 283 | 0.39328 | 293 | 0.015625 | 293 | 0.5984
[12 empty] | 268 | 0.08635 | 268 | 0.1161 | 274 | 0.015625 | 274 | 0.23825 | 284 | 0.015625 | 284 | 0.39071 | 294 | 0.015625 | 294 | 0.59654
[12 empty] | 269 | 0.08575 | 269 | 0.1152 | 275 | 0.015625 | 275 | 0.23682 | 285 | 0.015625 | 285 | 0.38814 | 295 | 0.015625 | 295 | 0.59468
[12 empty] | 270 | 0.08515 | 270 | 0.1143 | 276 | 0.015625 | 276 | 0.23538 | 286 | 0.015625 | 286 | 0.38557 | 296 | 0.015625 | 296 | 0.59282
[12 empty] | 271 | 0.08454 | 271 | 0.11341 | 277 | 0.015625 | 277 | 0.23394 | 287 | 0.015625 | 287 | 0.383 | 297 | 0.015625 | 297 | 0.59096
[12 empty] | 272 | 0.08394 | 272 | 0.11251 | 278 | 0.015625 | 278 | 0.2325 | 288 | 0.015625 | 288 | 0.38043 | 298 | 0.015625 | 298 | 0.5891
[12 empty] | 273 | 0.015625 | 273 | 0.11161 | 279 | 0.015625 | 279 | 0.23106 | 289 | 0.015625 | 289 | 0.37787 | 299 | 0.015625 | 299 | 0.57051
[12 empty] | 274 | 0.015625 | 274 | 0.111 | 280 | 0.015625 | 280 | 0.22963 | 290 | 0.015625 | 290 | 0.3753 | 300 | 0.015625 | 300 | 0.03334
[12 empty] | 275 | 0.015625 | 275 | 0.1104 | 281 | 0.015625 | 281 | 0.22819 | 291 | 0.015625 | 291 | 0.37273 | 453 | 0.015625 | 453 | 0.03334
[12 empty] | 276 | 0.015625 | 276 | 0.1098 | 282 | 0.015625 | 282 | 0.22675 | 292 | 0.015625 | 292 | 0.37016 | 454 | 0.011042 | 454 | 0.03334
[12 empty] | 277 | 0.015625 | 277 | 0.1092 | 283 | 0.015625 | 283 | 0.22531 | 293 | 0.015625 | 293 | 0.36759 | 455 | 0.001 | 455 | 0.03334
[12 empty] | 278 | 0.015625 | 278 | 0.10859 | 284 | 0.015625 | 284 | 0.22387 | 294 | 0.015625 | 294 | 0.36503 | 500 | 0.001 | 500 | 0.03334
[12 empty] | 279 | 0.015625 | 279 | 0.10799 | 285 | 0.015625 | 285 | 0.22244 | 295 | 0.015625 | 295 | 0.36246 | 501 | 0.001 | 501 | 0.01667
[12 empty] | 280 | 0.015625 | 280 | 0.10739 | 286 | 0.015625 | 286 | 0.221 | 296 | 0.015625 | 296 | 0.35989 | 6300 | 0.001 | 6300 | 0.01667
[12 empty] | 281 | 0.015625 | 281 | 0.10679 | 287 | 0.015625 | 287 | 0.21956 | 297 | 0.015625 | 297 | 0.35732
[12 empty] | 282 | 0.015625 | 282 | 0.10618 | 288 | 0.015625 | 288 | 0.21812 | 298 | 0.015625 | 298 | 0.35475
[12 empty] | 283 | 0.015625 | 283 | 0.10558 | 289 | 0.015625 | 289 | 0.21668 | 299 | 0.015625 | 299 | 0.35219
[12 empty] | 284 | 0.015625 | 284 | 0.10498 | 290 | 0.015625 | 290 | 0.21525 | 300 | 0.015625 | 300 | 0.03334
[12 empty] | 285 | 0.015625 | 285 | 0.10438 | 291 | 0.015625 | 291 | 0.21381 | 453 | 0.015625 | 453 | 0.03334
[12 empty] | 286 | 0.015625 | 286 | 0.10377 | 292 | 0.015625 | 292 | 0.21237 | 454 | 0.011042 | 454 | 0.03334
[12 empty] | 287 | 0.015625 | 287 | 0.10317 | 293 | 0.015625 | 293 | 0.21093 | 455 | 0.001 | 455 | 0.03334
[12 empty] | 288 | 0.015625 | 288 | 0.10257 | 294 | 0.015625 | 294 | 0.20949 | 500 | 0.001 | 500 | 0.03334
[12 empty] | 289 | 0.015625 | 289 | 0.10197 | 295 | 0.015625 | 295 | 0.20806 | 501 | 0.001 | 501 | 0.01667
[12 empty] | 290 | 0.015625 | 290 | 0.10136 | 296 | 0.015625 | 296 | 0.20662 | 6300 | 0.001 | 6300 | 0.01667
[12 empty] | 291 | 0.015625 | 291 | 0.10076 | 297 | 0.015625 | 297 | 0.20518
[12 empty] | 292 | 0.015625 | 292 | 0.10016 | 298 | 0.015625 | 298 | 0.20374
[12 empty] | 293 | 0.015625 | 293 | 0.09956 | 299 | 0.015625 | 299 | 0.2023
[12 empty] | 294 | 0.015625 | 294 | 0.09895 | 300 | 0.015625 | 300 | 0.03334
[12 empty] | 295 | 0.015625 | 295 | 0.09835 | 453 | 0.015625 | 453 | 0.03334
[12 empty] | 296 | 0.015625 | 296 | 0.09775 | 454 | 0.011042 | 454 | 0.03334
[12 empty] | 297 | 0.015625 | 297 | 0.09715 | 455 | 0.001 | 455 | 0.03334
[12 empty] | 298 | 0.015625 | 298 | 0.09654 | 500 | 0.001 | 500 | 0.03334
[12 empty] | 299 | 0.015625 | 299 | 0.09594 | 501 | 0.001 | 501 | 0.01667
[12 empty] | 300 | 0.015625 | 300 | 0.03334 | 6300 | 0.001 | 6300 | 0.01667
[12 empty] | 453 | 0.015625 | 453 | 0.03334
[12 empty] | 454 | 0.011042 | 454 | 0.03334
[12 empty] | 455 | 0.001 | 455 | 0.03334
[12 empty] | 500 | 0.001 | 500 | 0.03334
[12 empty] | 501 | 0.001 | 501 | 0.01667
[12 empty] | 6300 | 0.001 | 6300 | 0.01667

## S&C "T" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "T" Speed | [11 empty] | S&C "T" Speed | [11 empty] | S&C "T" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023
Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information.
2T |  |  |  | 3T |  |  |  | 5T |  |  |  | 6T |  |  |  | 8T |  |  |  | 10T |  |  |  | 12T |  |  |  | 15T |  |  |  | 20T
Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s
5 | 4.3796 | 5 | 10.9372 | 7 | 9.1805 | 7 | 26.3202 | 11 | 26.3858 | 11 | 67.1001 | 13 | 37.2281 | 13 | 103.1954 | 17 | 30.1342 | 17 | 111.8354 | 21 | 56.7922 | 21 | 654.617 | 28 | 50.1842 | 28 | 1639.2126 | 35 | 68.7779 | 35 | 1147.7552 | 44 | 67.2768 | 44 | 1477.1889
6 | 2.5641 | 6 | 4.3916 | 8 | 5.2827 | 8 | 9.1925 | 12 | 15.9002 | 12 | 26.3977 | 14 | 22.0735 | 14 | 37.2401 | 18 | 21.5908 | 18 | 48.2581 | 22 | 38.1731 | 22 | 106.5637 | 29 | 37.3107 | 29 | 146.4113 | 36 | 41.1932 | 36 | 188.6007 | 45 | 44.6028 | 45 | 243.4357
7 | 1.7345 | 7 | 2.5761 | 9 | 3.5826 | 9 | 5.2947 | 13 | 11.1254 | 13 | 15.9122 | 15 | 15.3806 | 15 | 22.0855 | 19 | 16.6332 | 19 | 30.1462 | 23 | 28.4492 | 23 | 56.8042 | 30 | 29.5023 | 30 | 75.3729 | 37 | 34.0933 | 37 | 101.4459 | 46 | 38.0029 | 46 | 131.31
8 | 1.2691 | 8 | 1.7465 | 10 | 2.6427 | 10 | 3.5946 | 14 | 8.4121 | 14 | 11.1374 | 16 | 9.237 | 16 | 15.3926 | 20 | 13.4051 | 20 | 21.6028 | 24 | 22.4872 | 24 | 38.1851 | 31 | 24.2674 | 31 | 50.1962 | 38 | 28.9759 | 38 | 68.7899 | 47 | 33.02 | 47 | 89.2852
9 | 0.97631 | 9 | 1.2811 | 11 | 2.0528 | 11 | 2.6547 | 15 | 6.6726 | 15 | 8.4241 | 17 | 7.5879 | 17 | 11.6396 | 21 | 11.1421 | 21 | 16.6452 | 25 | 15.5752 | 25 | 28.4612 | 32 | 20.518 | 32 | 37.3227 | 39 | 25.1152 | 39 | 51.7041 | 48 | 29.1269 | 48 | 67.2888
10 | 0.77795 | 10 | 0.98831 | 12 | 1.652 | 12 | 2.0648 | 16 | 4.5903 | 16 | 6.6846 | 18 | 6.3861 | 18 | 9.2491 | 22 | 9.472 | 22 | 13.4171 | 26 | 13.4012 | 26 | 22.4992 | 33 | 17.7035 | 33 | 29.5143 | 40 | 22.1012 | 40 | 41.2052 | 49 | 26.0027 | 49 | 53.7654
11 | 0.63635 | 11 | 0.78995 | 13 | 1.3643 | 13 | 1.664 | 17 | 3.9241 | 17 | 5.4807 | 19 | 5.4746 | 19 | 7.5999 | 23 | 8.1918 | 23 | 11.1541 | 27 | 11.7094 | 27 | 18.4777 | 34 | 15.5152 | 34 | 24.2794 | 41 | 19.6846 | 41 | 34.1053 | 50 | 23.4413 | 50 | 44.6148
12 | 0.53124 | 12 | 0.64835 | 14 | 1.1493 | 14 | 1.3763 | 18 | 3.4034 | 18 | 4.6024 | 20 | 4.7617 | 20 | 6.3981 | 24 | 7.1816 | 24 | 9.484 | 28 | 10.3575 | 28 | 15.5872 | 35 | 13.7669 | 35 | 20.53 | 42 | 17.7052 | 42 | 28.9879 | 51 | 21.3043 | 51 | 38.0149
13 | 0.45082 | 13 | 0.54324 | 15 | 0.98362 | 15 | 1.1613 | 19 | 2.9867 | 19 | 3.9361 | 21 | 4.1907 | 21 | 5.4866 | 25 | 5.6945 | 25 | 8.2038 | 29 | 9.2541 | 29 | 13.4132 | 36 | 11.1529 | 36 | 17.7155 | 43 | 16.0553 | 43 | 25.1272 | 52 | 19.495 | 52 | 33.032
14 | 0.38778 | 14 | 0.46282 | 16 | 0.74731 | 16 | 0.99562 | 20 | 2.6469 | 20 | 3.4154 | 22 | 3.7242 | 22 | 4.7737 | 26 | 5.1335 | 26 | 7.1936 | 30 | 8.3377 | 30 | 11.7214 | 37 | 10.152 | 37 | 15.5272 | 44 | 14.6597 | 44 | 22.1132 | 53 | 17.9441 | 53 | 29.1389
15 | 0.33734 | 15 | 0.39978 | 17 | 0.66091 | 17 | 0.86476 | 21 | 2.3652 | 21 | 2.9987 | 23 | 3.337 | 23 | 4.2027 | 27 | 4.6584 | 27 | 6.3778 | 31 | 7.5654 | 31 | 10.3695 | 38 | 9.2971 | 38 | 13.7789 | 45 | 12.4306 | 45 | 19.6966 | 54 | 16.6005 | 54 | 26.0147
16 | 0.26247 | 16 | 0.34934 | 18 | 0.58912 | 18 | 0.75931 | 22 | 2.1287 | 22 | 2.6589 | 24 | 3.0111 | 24 | 3.7362 | 28 | 4.2516 | 28 | 5.7065 | 32 | 6.9066 | 32 | 9.2661 | 39 | 8.5589 | 39 | 12.3514 | 46 | 11.5273 | 46 | 17.7172 | 55 | 14.3902 | 55 | 23.4533
17 | 0.23418 | 17 | 0.30832 | 19 | 0.52874 | 19 | 0.67291 | 23 | 1.9277 | 23 | 2.3772 | 25 | 2.4951 | 25 | 3.349 | 29 | 3.8999 | 29 | 5.1455 | 33 | 6.3386 | 33 | 8.3497 | 40 | 7.9157 | 40 | 11.1649 | 47 | 10.732 | 47 | 16.0673 | 56 | 13.471 | 56 | 21.3163
18 | 0.2103 | 18 | 0.27447 | 20 | 0.47742 | 20 | 0.60112 | 24 | 1.7552 | 24 | 2.1407 | 26 | 2.2882 | 26 | 3.0231 | 30 | 3.5932 | 30 | 4.6704 | 34 | 5.8444 | 34 | 7.5774 | 41 | 7.3506 | 41 | 10.164 | 48 | 10.0268 | 48 | 14.6717 | 57 | 12.6498 | 57 | 19.507
19 | 0.18993 | 19 | 0.24618 | 21 | 0.4334 | 21 | 0.54074 | 25 | 1.4755 | 25 | 1.9397 | 27 | 2.1073 | 27 | 2.7457 | 31 | 3.3238 | 31 | 4.2636 | 35 | 5.411 | 35 | 6.9186 | 42 | 6.8505 | 42 | 9.3091 | 49 | 9.3976 | 49 | 13.4767 | 58 | 11.9121 | 58 | 17.9561
20 | 0.17242 | 20 | 0.2223 | 22 | 0.39533 | 22 | 0.48942 | 26 | 1.3611 | 26 | 1.7672 | 28 | 1.948 | 28 | 2.5071 | 32 | 3.0856 | 32 | 3.9119 | 36 | 4.6879 | 36 | 6.3506 | 43 | 6.4051 | 43 | 8.5709 | 50 | 8.8329 | 50 | 12.4426 | 59 | 11.2459 | 59 | 16.6125
21 | 0.15725 | 21 | 0.20193 | 23 | 0.36216 | 23 | 0.4454 | 27 | 1.2599 | 27 | 1.6178 | 29 | 1.807 | 29 | 2.3002 | 33 | 2.8736 | 33 | 3.6052 | 37 | 4.3838 | 37 | 5.8564 | 44 | 6.0063 | 44 | 7.9277 | 51 | 8.3235 | 51 | 11.5393 | 60 | 10.6415 | 60 | 15.4377
22 | 0.14401 | 22 | 0.18442 | 24 | 0.33308 | 24 | 0.40733 | 28 | 1.1701 | 28 | 1.4875 | 30 | 1.6814 | 30 | 2.1193 | 34 | 2.684 | 34 | 3.3358 | 38 | 4.1105 | 38 | 5.423 | 45 | 5.3225 | 45 | 7.3626 | 52 | 7.862 | 52 | 10.744 | 61 | 10.0909 | 61 | 14.4022
23 | 0.13239 | 23 | 0.16925 | 25 | 0.28467 | 25 | 0.37416 | 29 | 1.0897 | 29 | 1.3731 | 31 | 1.569 | 31 | 1.96 | 35 | 2.5137 | 35 | 3.0976 | 39 | 3.8638 | 39 | 5.0402 | 46 | 5.0275 | 46 | 6.8625 | 53 | 7.4421 | 53 | 10.0388 | 62 | 9.5874 | 62 | 13.483
24 | 0.12214 | 24 | 0.15601 | 26 | 0.26438 | 26 | 0.34508 | 30 | 1.0177 | 30 | 1.2719 | 32 | 1.4679 | 32 | 1.819 | 36 | 2.2205 | 36 | 2.8856 | 40 | 3.6402 | 40 | 4.6999 | 47 | 4.7586 | 47 | 6.4171 | 54 | 7.0585 | 54 | 9.4096 | 63 | 9.1253 | 63 | 12.6618
25 | 0.10492 | 25 | 0.14439 | 27 | 0.24623 | 27 | 0.31942 | 31 | 0.95273 | 31 | 1.1821 | 33 | 1.3767 | 33 | 1.6934 | 37 | 2.0937 | 37 | 2.696 | 41 | 3.4367 | 41 | 4.3957 | 48 | 4.5126 | 48 | 6.0183 | 55 | 6.3836 | 55 | 8.8449 | 64 | 8.6999 | 64 | 11.9241
26 | 0.09766 | 26 | 0.13414 | 28 | 0.2299 | 28 | 0.29667 | 32 | 0.89398 | 32 | 1.1017 | 34 | 1.294 | 34 | 1.581 | 38 | 1.978 | 38 | 2.5257 | 42 | 3.2509 | 42 | 4.1225 | 49 | 4.2867 | 49 | 5.6592 | 56 | 6.0854 | 56 | 8.3355 | 65 | 7.9433 | 65 | 11.2578
27 | 0.09113 | 27 | 0.12504 | 29 | 0.21517 | 29 | 0.27638 | 33 | 0.84064 | 33 | 1.0297 | 35 | 1.2188 | 35 | 1.4799 | 39 | 1.872 | 39 | 2.3719 | 43 | 3.0807 | 43 | 3.8758 | 50 | 4.0787 | 50 | 5.3345 | 57 | 5.8095 | 57 | 7.874 | 66 | 7.6056 | 66 | 10.6535
28 | 0.08524 | 28 | 0.11692 | 30 | 0.20182 | 30 | 0.25823 | 34 | 0.79205 | 34 | 0.96473 | 36 | 1.0873 | 36 | 1.3887 | 40 | 1.7747 | 40 | 2.2325 | 44 | 2.9243 | 44 | 3.6522 | 51 | 3.8866 | 51 | 5.0395 | 58 | 5.5538 | 58 | 7.4541 | 67 | 7.2913 | 67 | 10.1029
29 | 0.0799 | 29 | 0.10966 | 31 | 0.1897 | 31 | 0.2419 | 35 | 0.74765 | 35 | 0.90598 | 37 | 1.0296 | 37 | 1.306 | 41 | 1.6851 | 41 | 2.1057 | 45 | 2.6471 | 45 | 3.4487 | 52 | 3.7089 | 52 | 4.7706 | 59 | 5.3161 | 59 | 7.0705 | 68 | 6.9982 | 68 | 9.5994
30 | 0.07505 | 30 | 0.10313 | 32 | 0.17864 | 32 | 0.22717 | 36 | 0.66957 | 36 | 0.85264 | 38 | 0.97657 | 38 | 1.2308 | 42 | 1.6023 | 42 | 1.99 | 46 | 2.5238 | 46 | 3.2629 | 53 | 3.5439 | 53 | 4.5245 | 60 | 5.0947 | 60 | 6.7189 | 69 | 6.7243 | 69 | 9.1373
31 | 0.07064 | 31 | 0.09724 | 33 | 0.16854 | 33 | 0.21382 | 37 | 0.63514 | 37 | 0.80405 | 39 | 0.92761 | 39 | 1.1621 | 43 | 1.5258 | 43 | 1.884 | 47 | 2.4093 | 47 | 3.0927 | 54 | 3.3905 | 54 | 4.2987 | 61 | 4.888 | 61 | 6.3956 | 70 | 6.4677 | 70 | 8.7119
32 | 0.0666 | 32 | 0.0919 | 34 | 0.15927 | 34 | 0.2017 | 38 | 0.60334 | 38 | 0.75965 | 40 | 0.88233 | 40 | 1.0993 | 44 | 1.4548 | 44 | 1.7867 | 48 | 2.3029 | 48 | 2.9363 | 55 | 3.114 | 55 | 4.0907 | 62 | 4.6946 | 62 | 6.0973 | 71 | 6.2271 | 71 | 8.319
33 | 0.0629 | 33 | 0.08705 | 35 | 0.15076 | 35 | 0.19064 | 39 | 0.57392 | 39 | 0.71896 | 41 | 0.84036 | 41 | 1.0416 | 45 | 1.3274 | 45 | 1.6971 | 49 | 2.2037 | 49 | 2.7922 | 56 | 2.989 | 56 | 3.8986 | 63 | 4.5134 | 63 | 5.8216 | 72 | 6.0009 | 72 | 7.9553
34 | 0.0595 | 34 | 0.08264 | 36 | 0.13567 | 36 | 0.18054 | 40 | 0.54663 | 40 | 0.68157 | 42 | 0.80139 | 42 | 0.98857 | 46 | 1.27 | 46 | 1.6143 | 50 | 2.111 | 50 | 2.6591 | 57 | 2.8719 | 57 | 3.7209 | 64 | 4.3434 | 64 | 5.5658 | 73 | 5.788 | 73 | 7.6176
35 | 0.05637 | 35 | 0.0786 | 37 | 0.12897 | 37 | 0.17127 | 41 | 0.52128 | 41 | 0.64714 | 43 | 0.76513 | 43 | 0.93961 | 47 | 1.2165 | 47 | 1.5378 | 51 | 2.0243 | 51 | 2.5358 | 58 | 2.762 | 58 | 3.5559 | 65 | 4.0329 | 65 | 5.3281 | 74 | 5.5873 | 74 | 7.3033
36 | 0.05082 | 36 | 0.0749 | 38 | 0.12276 | 38 | 0.16276 | 42 | 0.49768 | 42 | 0.61534 | 44 | 0.73132 | 44 | 0.89433 | 48 | 1.1663 | 48 | 1.4668 | 52 | 1.9431 | 52 | 2.4213 | 59 | 2.6586 | 59 | 3.4025 | 66 | 3.8909 | 66 | 5.1067 | 75 | 5.3978 | 75 | 7.0102
37 | 0.04834 | 37 | 0.0715 | 39 | 0.11699 | 39 | 0.15491 | 43 | 0.47567 | 43 | 0.58592 | 45 | 0.67023 | 45 | 0.85236 | 49 | 1.1193 | 49 | 1.4008 | 53 | 1.8669 | 53 | 2.3149 | 60 | 2.5613 | 60 | 3.2595 | 67 | 3.7568 | 67 | 4.8999 | 76 | 5.0489 | 76 | 6.7363
38 | 0.04604 | 38 | 0.06837 | 40 | 0.11162 | 40 | 0.14767 | 44 | 0.45511 | 44 | 0.55863 | 46 | 0.64257 | 46 | 0.81339 | 50 | 1.0751 | 50 | 1.3394 | 54 | 1.7952 | 54 | 2.2157 | 61 | 2.4695 | 61 | 3.126 | 68 | 3.63 | 68 | 4.7066 | 77 | 4.8881 | 77 | 6.4797
39 | 0.04391 | 39 | 0.06549 | 41 | 0.10661 | 41 | 0.14097 | 45 | 0.41785 | 45 | 0.53328 | 47 | 0.61661 | 47 | 0.77713 | 51 | 1.0336 | 51 | 1.282 | 55 | 1.6642 | 55 | 2.123 | 62 | 2.3828 | 62 | 3.001 | 69 | 3.5099 | 69 | 4.5254 | 78 | 4.7355 | 78 | 6.2391
40 | 0.04192 | 40 | 0.06282 | 42 | 0.10193 | 42 | 0.13476 | 46 | 0.40093 | 46 | 0.50968 | 48 | 0.59223 | 48 | 0.74332 | 52 | 0.99446 | 52 | 1.2285 | 56 | 1.6042 | 56 | 2.0363 | 63 | 2.3008 | 63 | 2.8839 | 70 | 3.3961 | 70 | 4.3554 | 79 | 4.5906 | 79 | 6.0129
41 | 0.04006 | 41 | 0.06034 | 43 | 0.09756 | 43 | 0.12899 | 47 | 0.38503 | 47 | 0.48767 | 49 | 0.56929 | 49 | 0.71175 | 53 | 0.95759 | 53 | 1.1783 | 57 | 1.5475 | 57 | 1.9551 | 64 | 2.2232 | 64 | 2.774 | 71 | 3.288 | 71 | 4.1955 | 80 | 4.4527 | 80 | 5.8
42 | 0.03832 | 42 | 0.05804 | 44 | 0.09347 | 44 | 0.12362 | 48 | 0.37008 | 48 | 0.46711 | 50 | 0.54768 | 50 | 0.68223 | 54 | 0.92278 | 54 | 1.1313 | 58 | 1.4938 | 58 | 1.8789 | 65 | 2.0799 | 65 | 2.6706 | 72 | 3.1854 | 72 | 4.0449 | 81 | 4.3214 | 81 | 5.5993
43 | 0.03669 | 43 | 0.05591 | 45 | 0.08602 | 45 | 0.11861 | 49 | 0.35598 | 49 | 0.44787 | 51 | 0.52729 | 51 | 0.65457 | 55 | 0.85875 | 55 | 1.0871 | 59 | 1.443 | 59 | 1.8072 | 66 | 2.0136 | 66 | 2.5733 | 73 | 3.0878 | 73 | 3.9029 | 82 | 4.1962 | 82 | 5.4097
44 | 0.03517 | 44 | 0.05392 | 46 | 0.08262 | 46 | 0.11393 | 50 | 0.34269 | 50 | 0.42985 | 52 | 0.50804 | 52 | 0.62861 | 56 | 0.82926 | 56 | 1.0456 | 60 | 1.3948 | 60 | 1.7398 | 67 | 1.9506 | 67 | 2.4815 | 74 | 2.9949 | 74 | 3.7688 | 83 | 4.0769 | 83 | 5.2306
45 | 0.015625 | 45 | 0.05206 | 47 | 0.07943 | 47 | 0.10956 | 51 | 0.33014 | 51 | 0.41293 | 53 | 0.48984 | 53 | 0.60423 | 57 | 0.80129 | 57 | 1.0065 | 61 | 1.3491 | 61 | 1.6762 | 68 | 1.8906 | 68 | 2.3948 | 75 | 2.9063 | 75 | 3.642 | 84 | 3.9629 | 84 | 5.0609
46 | 0.015625 | 46 | 0.05032 | 48 | 0.07641 | 48 | 0.10547 | 52 | 0.31827 | 52 | 0.39703 | 54 | 0.47262 | 54 | 0.58129 | 58 | 0.77474 | 58 | 0.96959 | 62 | 1.3057 | 62 | 1.6162 | 69 | 1.8335 | 69 | 2.3128 | 76 | 2.7412 | 76 | 3.5219 | 85 | 3.7498 | 85 | 4.9001
47 | 0.015625 | 47 | 0.04869 | 49 | 0.07357 | 49 | 0.10162 | 53 | 0.30703 | 53 | 0.38208 | 55 | 0.44082 | 55 | 0.55968 | 59 | 0.74952 | 59 | 0.93478 | 63 | 1.2643 | 63 | 1.5595 | 70 | 1.779 | 70 | 2.2352 | 77 | 2.6642 | 77 | 3.4081 | 86 | 3.65 | 86 | 4.7475
48 | 0.015625 | 48 | 0.04717 | 50 | 0.07088 | 50 | 0.09802 | 54 | 0.29639 | 54 | 0.36798 | 56 | 0.42613 | 56 | 0.53929 | 60 | 0.72554 | 60 | 0.90188 | 64 | 1.225 | 64 | 1.5058 | 71 | 1.7271 | 71 | 2.1617 | 78 | 2.5906 | 78 | 3.3 | 87 | 3.5545 | 87 | 4.6026
49 | 0.015625 | 49 | 0.04574 | 51 | 0.06834 | 51 | 0.09462 | 55 | 0.27671 | 55 | 0.35469 | 57 | 0.41217 | 57 | 0.52004 | 61 | 0.70271 | 61 | 0.87075 | 65 | 1.1518 | 65 | 1.455 | 72 | 1.6774 | 72 | 2.0919 | 79 | 2.5201 | 79 | 3.1974 | 88 | 3.4629 | 88 | 4.4647
50 | 0.015625 | 50 | 0.03334 | 52 | 0.06593 | 52 | 0.09143 | 56 | 0.26761 | 56 | 0.34214 | 58 | 0.39889 | 58 | 0.50184 | 62 | 0.68096 | 62 | 0.84126 | 66 | 1.1177 | 66 | 1.4068 | 73 | 1.63 | 73 | 2.0256 | 80 | 2.4526 | 80 | 3.0998 | 89 | 3.3751 | 89 | 4.3334
453 | 0.015625 | 453 | 0.03334 | 53 | 0.06365 | 53 | 0.08841 | 57 | 0.25895 | 57 | 0.33027 | 59 | 0.38625 | 59 | 0.48462 | 63 | 0.66022 | 63 | 0.81329 | 67 | 1.0851 | 67 | 1.3611 | 74 | 1.5846 | 74 | 1.9626 | 81 | 2.3879 | 81 | 3.0069 | 90 | 3.2907 | 90 | 4.2082
454 | 0.011042 | 454 | 0.03334 | 54 | 0.06149 | 54 | 0.08557 | 58 | 0.2507 | 58 | 0.31903 | 60 | 0.37421 | 60 | 0.4683 | 64 | 0.64043 | 64 | 0.78674 | 68 | 1.0539 | 68 | 1.3177 | 75 | 1.5412 | 75 | 1.9026 | 82 | 2.3258 | 82 | 2.9183 | 91 | 3.2097 | 91 | 4.0888
455 | 0.001 | 455 | 0.03334 | 55 | 0.05748 | 55 | 0.08288 | 59 | 0.24285 | 59 | 0.30839 | 61 | 0.36273 | 61 | 0.45282 | 65 | 0.60347 | 65 | 0.76152 | 69 | 1.0242 | 69 | 1.2763 | 76 | 1.4597 | 76 | 1.8455 | 83 | 2.2663 | 83 | 2.8339 | 92 | 3.1318 | 92 | 3.9749
500 | 0.001 | 500 | 0.03334 | 56 | 0.05562 | 56 | 0.08034 | 60 | 0.23537 | 60 | 0.29829 | 62 | 0.35177 | 62 | 0.43813 | 66 | 0.5862 | 66 | 0.73754 | 70 | 0.99566 | 70 | 1.237 | 77 | 1.4214 | 77 | 1.791 | 84 | 2.2091 | 84 | 2.7532 | 93 | 3.0569 | 93 | 3.866
501 | 0.001 | 501 | 0.01667 | 57 | 0.05385 | 57 | 0.07793 | 61 | 0.22822 | 61 | 0.28871 | 63 | 0.34131 | 63 | 0.42417 | 67 | 0.56967 | 67 | 0.71471 | 71 | 0.96835 | 71 | 1.1995 | 78 | 1.3847 | 78 | 1.7391 | 85 | 2.1013 | 85 | 2.6762 | 94 | 2.9848 | 94 | 3.7618
6300 | 0.001 | 6300 | 0.01667 | 58 | 0.05216 | 58 | 0.07565 | 62 | 0.2214 | 62 | 0.27961 | 64 | 0.33132 | 64 | 0.41089 | 68 | 0.55385 | 68 | 0.69296 | 72 | 0.94218 | 72 | 1.1638 | 79 | 1.3494 | 79 | 1.6894 | 86 | 2.0505 | 86 | 2.6026 | 95 | 2.8484 | 95 | 3.662
|  |  |  | 59 | 0.05055 | 59 | 0.07349 | 63 | 0.21489 | 63 | 0.27095 | 65 | 0.31261 | 65 | 0.39825 | 69 | 0.53868 | 69 | 0.67222 | 73 | 0.91707 | 73 | 1.1297 | 80 | 1.3155 | 80 | 1.642 | 87 | 2.0016 | 87 | 2.5321 | 96 | 2.7839 | 96 | 3.5665
|  |  |  | 60 | 0.04902 | 60 | 0.07143 | 64 | 0.20866 | 64 | 0.2627 | 66 | 0.30385 | 66 | 0.38621 | 70 | 0.52413 | 70 | 0.65243 | 74 | 0.89298 | 74 | 1.0971 | 81 | 1.2829 | 81 | 1.5966 | 88 | 1.9545 | 88 | 2.4646 | 97 | 2.7217 | 97 | 3.4749
|  |  |  | 61 | 0.04755 | 61 | 0.06948 | 65 | 0.19699 | 65 | 0.25485 | 67 | 0.29546 | 67 | 0.37473 | 71 | 0.51018 | 71 | 0.63353 | 75 | 0.86984 | 75 | 1.0659 | 82 | 1.2515 | 82 | 1.5532 | 89 | 1.909 | 89 | 2.3999 | 98 | 2.6616 | 98 | 3.3871
|  |  |  | 62 | 0.04615 | 62 | 0.06762 | 66 | 0.19152 | 66 | 0.24737 | 68 | 0.28741 | 68 | 0.36377 | 72 | 0.49678 | 72 | 0.61547 | 76 | 0.82624 | 76 | 1.0362 | 83 | 1.2213 | 83 | 1.5115 | 90 | 1.8653 | 90 | 2.3378 | 99 | 2.6037 | 99 | 3.3027
|  |  |  | 63 | 0.04481 | 63 | 0.06585 | 67 | 0.18628 | 67 | 0.24022 | 69 | 0.2797 | 69 | 0.35331 | 73 | 0.48391 | 73 | 0.5982 | 77 | 0.80568 | 77 | 1.0077 | 84 | 1.1923 | 84 | 1.4717 | 91 | 1.823 | 91 | 2.2783 | 100 | 2.5477 | 100 | 3.2217
|  |  |  | 64 | 0.04353 | 64 | 0.06416 | 68 | 0.18125 | 68 | 0.2334 | 70 | 0.27229 | 70 | 0.34332 | 74 | 0.47154 | 74 | 0.58167 | 78 | 0.7859 | 78 | 0.98035 | 85 | 1.1372 | 85 | 1.4334 | 92 | 1.7823 | 92 | 2.2211 | 101 | 2.4935 | 101 | 3.1438
|  |  |  | 65 | 0.04113 | 65 | 0.06255 | 69 | 0.17642 | 69 | 0.22689 | 71 | 0.26517 | 71 | 0.33376 | 75 | 0.45965 | 75 | 0.56585 | 79 | 0.76685 | 79 | 0.95418 | 86 | 1.1111 | 86 | 1.3967 | 93 | 1.7429 | 93 | 2.1662 | 102 | 2.4412 | 102 | 3.0689
|  |  |  | 66 | 0.04 | 66 | 0.06102 | 70 | 0.17178 | 70 | 0.22066 | 72 | 0.25833 | 72 | 0.32461 | 76 | 0.43718 | 76 | 0.55068 | 80 | 0.74849 | 80 | 0.92907 | 87 | 1.086 | 87 | 1.3614 | 94 | 1.7049 | 94 | 2.1133 | 103 | 2.3906 | 103 | 2.9968
|  |  |  | 67 | 0.03892 | 67 | 0.05955 | 71 | 0.16733 | 71 | 0.2147 | 73 | 0.25175 | 73 | 0.31585 | 77 | 0.42657 | 77 | 0.53613 | 81 | 0.7308 | 81 | 0.90498 | 88 | 1.0617 | 88 | 1.3275 | 95 | 1.6326 | 95 | 2.0625 | 104 | 2.3416 | 104 | 2.9273
|  |  |  | 68 | 0.03788 | 68 | 0.05815 | 72 | 0.16305 | 72 | 0.20899 | 74 | 0.24543 | 74 | 0.30746 | 78 | 0.41635 | 78 | 0.52218 | 82 | 0.71374 | 82 | 0.88184 | 89 | 1.0382 | 89 | 1.2949 | 96 | 1.5983 | 96 | 2.0136 | 105 | 2.2482 | 105 | 2.8604
|  |  |  | 69 | 0.03688 | 69 | 0.05681 | 73 | 0.15893 | 73 | 0.20352 | 75 | 0.23934 | 75 | 0.29941 | 79 | 0.40649 | 79 | 0.50878 | 83 | 0.69728 | 83 | 0.85961 | 90 | 1.0156 | 90 | 1.2635 | 97 | 1.565 | 97 | 1.9665 | 106 | 2.2037 | 106 | 2.7959
|  |  |  | 70 | 0.03592 | 70 | 0.05553 | 74 | 0.15496 | 74 | 0.19828 | 76 | 0.22783 | 76 | 0.2917 | 80 | 0.39698 | 80 | 0.49591 | 84 | 0.68139 | 84 | 0.83824 | 91 | 0.99366 | 91 | 1.2333 | 98 | 1.5328 | 98 | 1.921 | 107 | 2.1606 | 107 | 2.7337
|  |  |  | 71 | 0.035 | 71 | 0.0543 | 75 | 0.15115 | 75 | 0.19325 | 77 | 0.22238 | 77 | 0.28429 | 81 | 0.38781 | 81 | 0.48354 | 85 | 0.65123 | 85 | 0.81768 | 92 | 0.97246 | 92 | 1.2043 | 99 | 1.5016 | 99 | 1.8773 | 108 | 2.1188 | 108 | 2.6736
|  |  |  | 72 | 0.03412 | 72 | 0.05313 | 76 | 0.14393 | 76 | 0.18842 | 78 | 0.21713 | 78 | 0.27717 | 82 | 0.37895 | 82 | 0.47165 | 86 | 0.6369 | 86 | 0.7979 | 93 | 0.95196 | 93 | 1.1762 | 100 | 1.4714 | 100 | 1.835 | 109 | 2.0782 | 109 | 2.6157
|  |  |  | 73 | 0.03326 | 73 | 0.052 | 77 | 0.14051 | 77 | 0.18378 | 79 | 0.21207 | 79 | 0.27033 | 83 | 0.37039 | 83 | 0.4602 | 87 | 0.62305 | 87 | 0.77885 | 94 | 0.9321 | 94 | 1.1492 | 101 | 1.4422 | 101 | 1.7943 | 110 | 2.0388 | 110 | 2.5597
|  |  |  | 74 | 0.015625 | 74 | 0.05092 | 78 | 0.13721 | 78 | 0.17933 | 80 | 0.20718 | 80 | 0.26375 | 84 | 0.36213 | 84 | 0.44918 | 88 | 0.60966 | 88 | 0.76049 | 95 | 0.89426 | 95 | 1.1231 | 102 | 1.4138 | 102 | 1.7549 | 111 | 2.0006 | 111 | 2.5055
|  |  |  | 75 | 0.015625 | 75 | 0.04988 | 79 | 0.13403 | 79 | 0.17505 | 81 | 0.20245 | 81 | 0.25743 | 85 | 0.34642 | 85 | 0.43857 | 89 | 0.59669 | 89 | 0.7428 | 96 | 0.87622 | 96 | 1.098 | 103 | 1.3863 | 103 | 1.7169 | 112 | 1.9635 | 112 | 2.4532
|  |  |  | 76 | 0.015625 | 76 | 0.04888 | 80 | 0.13096 | 80 | 0.17093 | 82 | 0.19789 | 82 | 0.25134 | 86 | 0.33895 | 86 | 0.42835 | 90 | 0.58415 | 90 | 0.72574 | 97 | 0.85873 | 97 | 1.0737 | 104 | 1.3596 | 104 | 1.6802 | 113 | 1.9275 | 113 | 2.4026
|  |  |  | 77 | 0.015625 | 77 | 0.04792 | 81 | 0.128 | 81 | 0.16696 | 83 | 0.19349 | 83 | 0.24548 | 87 | 0.33171 | 87 | 0.41849 | 91 | 0.572 | 91 | 0.70928 | 98 | 0.84177 | 98 | 1.0502 | 105 | 1.3085 | 105 | 1.6446 | 114 | 1.8925 | 114 | 2.3536
|  |  |  | 78 | 0.015625 | 78 | 0.047 | 82 | 0.12513 | 82 | 0.16315 | 84 | 0.18923 | 84 | 0.23983 | 88 | 0.32472 | 88 | 0.40898 | 92 | 0.56023 | 92 | 0.69339 | 99 | 0.82531 | 99 | 1.0276 | 106 | 1.2841 | 106 | 1.6103 | 115 | 1.8254 | 115 | 2.3062
|  |  |  | 79 | 0.015625 | 79 | 0.04612 | 83 | 0.12236 | 83 | 0.15947 | 85 | 0.18112 | 85 | 0.23438 | 89 | 0.31794 | 89 | 0.39981 | 93 | 0.54882 | 93 | 0.67805 | 100 | 0.80935 | 100 | 1.0057 | 107 | 1.2603 | 107 | 1.577 | 116 | 1.7932 | 116 | 2.2602
|  |  |  | 80 | 0.015625 | 80 | 0.04526 | 84 | 0.11968 | 84 | 0.15593 | 86 | 0.17726 | 86 | 0.22913 | 90 | 0.31137 | 90 | 0.39095 | 94 | 0.53777 | 94 | 0.66323 | 101 | 0.79385 | 101 | 0.98446 | 108 | 1.2373 | 108 | 1.5448 | 117 | 1.7619 | 117 | 2.2157
|  |  |  | 81 | 0.015625 | 81 | 0.03334 | 85 | 0.11458 | 85 | 0.15251 | 87 | 0.17352 | 87 | 0.22407 | 91 | 0.30501 | 91 | 0.38239 | 95 | 0.51665 | 95 | 0.6489 | 102 | 0.77881 | 102 | 0.96396 | 109 | 1.2148 | 109 | 1.5136 | 118 | 1.7314 | 118 | 2.1726
|  |  |  | 453 | 0.015625 | 453 | 0.03334 | 86 | 0.11215 | 86 | 0.14921 | 88 | 0.16991 | 88 | 0.21918 | 92 | 0.29884 | 92 | 0.37413 | 96 | 0.50656 | 96 | 0.63505 | 103 | 0.76419 | 103 | 0.9441 | 110 | 1.193 | 110 | 1.4834 | 119 | 1.7018 | 119 | 2.1308
|  |  |  | 454 | 0.011042 | 454 | 0.03334 | 87 | 0.1098 | 87 | 0.14603 | 89 | 0.1664 | 89 | 0.21445 | 93 | 0.29286 | 93 | 0.36614 | 97 | 0.49676 | 97 | 0.62166 | 104 | 0.74999 | 104 | 0.92488 | 111 | 1.1718 | 111 | 1.4542 | 120 | 1.6729 | 120 | 2.0902
|  |  |  | 455 | 0.001 | 455 | 0.03334 | 88 | 0.10752 | 88 | 0.14296 | 90 | 0.163 | 90 | 0.20989 | 94 | 0.28705 | 94 | 0.35842 | 98 | 0.48725 | 98 | 0.60869 | 105 | 0.72278 | 105 | 0.90626 | 112 | 1.1512 | 112 | 1.4258 | 121 | 1.6448 | 121 | 2.0508
|  |  |  | 500 | 0.001 | 500 | 0.03334 | 89 | 0.10532 | 89 | 0.14 | 91 | 0.15971 | 91 | 0.20549 | 95 | 0.27596 | 95 | 0.35095 | 99 | 0.47802 | 99 | 0.59615 | 106 | 0.70974 | 106 | 0.88822 | 113 | 1.1311 | 113 | 1.3983 | 122 | 1.6174 | 122 | 2.0126
|  |  |  | 501 | 0.001 | 501 | 0.01667 | 90 | 0.10318 | 90 | 0.13713 | 92 | 0.15651 | 92 | 0.20123 | 96 | 0.27065 | 96 | 0.34371 | 100 | 0.46904 | 100 | 0.584 | 107 | 0.69705 | 107 | 0.87073 | 114 | 1.1116 | 114 | 1.3716 | 123 | 1.5907 | 123 | 1.9755
|  |  |  | 6300 | 0.001 | 6300 | 0.01667 | 91 | 0.1011 | 91 | 0.13436 | 93 | 0.15341 | 93 | 0.19711 | 97 | 0.2655 | 97 | 0.33672 | 101 | 0.46032 | 101 | 0.57223 | 108 | 0.68471 | 108 | 0.85377 | 115 | 1.074 | 115 | 1.3457 | 124 | 1.5647 | 124 | 1.9395
[8 empty] | 92 | 0.09909 | 92 | 0.13168 | 94 | 0.1504 | 94 | 0.19312 | 98 | 0.26049 | 98 | 0.32994 | 102 | 0.45185 | 102 | 0.56082 | 109 | 0.67269 | 109 | 0.83731 | 116 | 1.056 | 116 | 1.3205 | 125 | 1.5147 | 125 | 1.9045
[8 empty] | 93 | 0.09713 | 93 | 0.12909 | 95 | 0.14465 | 95 | 0.18926 | 99 | 0.25563 | 99 | 0.32337 | 103 | 0.44361 | 103 | 0.54977 | 110 | 0.661 | 110 | 0.82135 | 117 | 1.0384 | 117 | 1.2961 | 126 | 1.4905 | 126 | 1.8704
[8 empty] | 94 | 0.09524 | 94 | 0.12658 | 96 | 0.1419 | 96 | 0.18552 | 100 | 0.2509 | 100 | 0.31701 | 104 | 0.43559 | 104 | 0.53905 | 111 | 0.64961 | 111 | 0.80585 | 118 | 1.0213 | 118 | 1.2723 | 127 | 1.467 | 127 | 1.8374
[8 empty] | 95 | 0.09161 | 95 | 0.12415 | 97 | 0.13922 | 97 | 0.18191 | 101 | 0.2463 | 101 | 0.31084 | 105 | 0.42021 | 105 | 0.52865 | 112 | 0.63852 | 112 | 0.79081 | 119 | 1.0046 | 119 | 1.2493 | 128 | 1.4441 | 128 | 1.8052
[8 empty] | 96 | 0.08987 | 96 | 0.1218 | 98 | 0.13662 | 98 | 0.1784 | 102 | 0.24183 | 102 | 0.30486 | 106 | 0.41282 | 106 | 0.51856 | 113 | 0.62772 | 113 | 0.77619 | 120 | 0.98825 | 120 | 1.2268 | 129 | 1.4217 | 129 | 1.7739
[8 empty] | 97 | 0.08819 | 97 | 0.11952 | 99 | 0.13409 | 99 | 0.175 | 103 | 0.23748 | 103 | 0.29905 | 107 | 0.40563 | 107 | 0.50876 | 114 | 0.61719 | 114 | 0.76199 | 121 | 0.97236 | 121 | 1.205 | 130 | 1.3998 | 130 | 1.7434
[8 empty] | 98 | 0.08655 | 98 | 0.11732 | 100 | 0.13163 | 100 | 0.17171 | 104 | 0.23324 | 104 | 0.29342 | 108 | 0.39863 | 108 | 0.49925 | 115 | 0.59692 | 115 | 0.7482 | 122 | 0.95685 | 122 | 1.1838 | 131 | 1.3785 | 131 | 1.7138
[8 empty] | 99 | 0.08495 | 99 | 0.11518 | 101 | 0.12924 | 101 | 0.16851 | 105 | 0.22511 | 105 | 0.28796 | 109 | 0.39181 | 109 | 0.49002 | 116 | 0.58717 | 116 | 0.73478 | 123 | 0.94173 | 123 | 1.1632 | 132 | 1.3576 | 132 | 1.6849
[8 empty] | 100 | 0.0834 | 100 | 0.1131 | 102 | 0.12692 | 102 | 0.16541 | 106 | 0.22121 | 106 | 0.28265 | 110 | 0.38516 | 110 | 0.48104 | 117 | 0.57766 | 117 | 0.72174 | 124 | 0.92696 | 124 | 1.1431 | 133 | 1.3372 | 133 | 1.6568
[8 empty] | 101 | 0.08189 | 101 | 0.11109 | 103 | 0.12465 | 103 | 0.1624 | 107 | 0.2174 | 107 | 0.2775 | 111 | 0.37868 | 111 | 0.47232 | 118 | 0.56838 | 118 | 0.70905 | 125 | 0.89848 | 125 | 1.1236 | 134 | 1.3173 | 134 | 1.6294
[8 empty] | 102 | 0.08042 | 102 | 0.10913 | 104 | 0.12245 | 104 | 0.15948 | 108 | 0.21369 | 108 | 0.27249 | 112 | 0.37237 | 112 | 0.46385 | 119 | 0.55932 | 119 | 0.69671 | 126 | 0.88473 | 126 | 1.1046 | 135 | 1.2979 | 135 | 1.6027
[8 empty] | 103 | 0.07899 | 103 | 0.10724 | 105 | 0.11821 | 105 | 0.15665 | 109 | 0.21008 | 109 | 0.26763 | 113 | 0.36622 | 113 | 0.45561 | 120 | 0.55048 | 120 | 0.68469 | 127 | 0.87131 | 127 | 1.086 | 136 | 1.2603 | 136 | 1.5767
[8 empty] | 104 | 0.0776 | 104 | 0.1054 | 106 | 0.11618 | 106 | 0.1539 | 110 | 0.20656 | 110 | 0.2629 | 114 | 0.36021 | 114 | 0.44759 | 121 | 0.54186 | 121 | 0.673 | 128 | 0.8582 | 128 | 1.068 | 137 | 1.2422 | 137 | 1.5514
[8 empty] | 105 | 0.07493 | 105 | 0.10361 | 107 | 0.1142 | 107 | 0.15122 | 111 | 0.20313 | 111 | 0.2583 | 115 | 0.34865 | 115 | 0.43979 | 122 | 0.53344 | 122 | 0.66161 | 129 | 0.84538 | 129 | 1.0504 | 138 | 1.2244 | 138 | 1.5267
[8 empty] | 106 | 0.07364 | 106 | 0.10187 | 108 | 0.11226 | 108 | 0.14862 | 112 | 0.19978 | 112 | 0.25383 | 116 | 0.34307 | 116 | 0.43221 | 123 | 0.52521 | 123 | 0.65052 | 130 | 0.83286 | 130 | 1.0333 | 139 | 1.207 | 139 | 1.5025
[8 empty] | 107 | 0.07239 | 107 | 0.10019 | 109 | 0.11038 | 109 | 0.14609 | 113 | 0.19651 | 113 | 0.24948 | 117 | 0.33763 | 117 | 0.42482 | 124 | 0.51718 | 124 | 0.63972 | 131 | 0.82062 | 131 | 1.0166 | 140 | 1.19 | 140 | 1.479
[8 empty] | 108 | 0.07117 | 108 | 0.09855 | 110 | 0.10854 | 110 | 0.14363 | 114 | 0.19333 | 114 | 0.24524 | 118 | 0.33232 | 118 | 0.41763 | 125 | 0.50166 | 125 | 0.62919 | 132 | 0.80865 | 132 | 1.0003 | 141 | 1.1734 | 141 | 1.4561
[8 empty] | 109 | 0.06998 | 109 | 0.09695 | 111 | 0.10675 | 111 | 0.14124 | 115 | 0.18719 | 115 | 0.24112 | 119 | 0.32714 | 119 | 0.41063 | 126 | 0.49417 | 126 | 0.61893 | 133 | 0.79694 | 133 | 0.98436 | 142 | 1.1571 | 142 | 1.4337
[8 empty] | 110 | 0.06882 | 110 | 0.0954 | 112 | 0.10501 | 112 | 0.13892 | 116 | 0.18423 | 116 | 0.23711 | 120 | 0.32208 | 120 | 0.40381 | 127 | 0.48684 | 127 | 0.60892 | 134 | 0.78549 | 134 | 0.96885 | 143 | 1.1412 | 143 | 1.4118
[8 empty] | 111 | 0.06769 | 111 | 0.09389 | 113 | 0.1033 | 113 | 0.13665 | 117 | 0.18134 | 117 | 0.23321 | 121 | 0.31713 | 121 | 0.39716 | 128 | 0.47968 | 128 | 0.59917 | 135 | 0.7743 | 135 | 0.95373 | 144 | 1.1256 | 144 | 1.3905
[8 empty] | 112 | 0.06658 | 112 | 0.09242 | 114 | 0.10164 | 114 | 0.13445 | 118 | 0.17851 | 118 | 0.2294 | 122 | 0.3123 | 122 | 0.39068 | 129 | 0.47268 | 129 | 0.58966 | 136 | 0.75262 | 136 | 0.93896 | 145 | 1.0953 | 145 | 1.3696
[8 empty] | 113 | 0.06551 | 113 | 0.09099 | 115 | 0.09843 | 115 | 0.1323 | 119 | 0.17576 | 119 | 0.22569 | 123 | 0.30758 | 123 | 0.38437 | 130 | 0.46583 | 130 | 0.58038 | 137 | 0.74213 | 137 | 0.92455 | 146 | 1.0807 | 146 | 1.3492
[8 empty] | 114 | 0.06446 | 114 | 0.0896 | 116 | 0.09689 | 116 | 0.13021 | 120 | 0.17306 | 120 | 0.22208 | 124 | 0.30296 | 124 | 0.37822 | 131 | 0.45913 | 131 | 0.57132 | 138 | 0.73186 | 138 | 0.91048 | 147 | 1.0663 | 147 | 1.3293
[8 empty] | 115 | 0.06243 | 115 | 0.08825 | 117 | 0.09538 | 117 | 0.12818 | 121 | 0.17043 | 121 | 0.21856 | 125 | 0.29404 | 125 | 0.37221 | 132 | 0.45258 | 132 | 0.56248 | 139 | 0.7218 | 139 | 0.89673 | 148 | 1.0523 | 148 | 1.3099
[8 empty] | 116 | 0.06145 | 116 | 0.08693 | 118 | 0.0939 | 118 | 0.1262 | 122 | 0.16786 | 122 | 0.21513 | 126 | 0.28973 | 126 | 0.36636 | 133 | 0.44616 | 133 | 0.55386 | 140 | 0.71195 | 140 | 0.88331 | 149 | 1.0385 | 149 | 1.2909
[8 empty] | 117 | 0.0605 | 117 | 0.08564 | 119 | 0.09246 | 119 | 0.12426 | 123 | 0.16535 | 123 | 0.21178 | 127 | 0.28551 | 127 | 0.36065 | 134 | 0.43989 | 134 | 0.54544 | 141 | 0.70231 | 141 | 0.8702 | 150 | 1.025 | 150 | 1.2723
[8 empty] | 118 | 0.05956 | 118 | 0.08439 | 120 | 0.09105 | 120 | 0.12238 | 124 | 0.16289 | 124 | 0.20851 | 128 | 0.28139 | 128 | 0.35507 | 135 | 0.43375 | 135 | 0.53721 | 142 | 0.69287 | 142 | 0.85738 | 151 | 1.0118 | 151 | 1.2542
[8 empty] | 119 | 0.05865 | 119 | 0.08317 | 121 | 0.08968 | 121 | 0.12054 | 125 | 0.15814 | 125 | 0.20533 | 129 | 0.27735 | 129 | 0.34963 | 136 | 0.42184 | 136 | 0.52918 | 143 | 0.68361 | 143 | 0.84486 | 152 | 0.99879 | 152 | 1.2364
[8 empty] | 120 | 0.05776 | 120 | 0.08198 | 122 | 0.08833 | 122 | 0.11875 | 126 | 0.15584 | 126 | 0.20222 | 130 | 0.2734 | 130 | 0.34432 | 137 | 0.41608 | 137 | 0.52133 | 144 | 0.67455 | 144 | 0.83262 | 153 | 0.98607 | 153 | 1.219
[8 empty] | 121 | 0.05689 | 121 | 0.08082 | 123 | 0.08702 | 123 | 0.11701 | 127 | 0.15359 | 127 | 0.19919 | 131 | 0.26954 | 131 | 0.33914 | 138 | 0.41043 | 138 | 0.51366 | 145 | 0.65696 | 145 | 0.82065 | 154 | 0.9736 | 154 | 1.202
[8 empty] | 122 | 0.05604 | 122 | 0.07969 | 124 | 0.08573 | 124 | 0.1153 | 128 | 0.15139 | 128 | 0.19623 | 132 | 0.26575 | 132 | 0.33408 | 139 | 0.4049 | 139 | 0.50617 | 146 | 0.64842 | 146 | 0.80894 | 155 | 0.96137 | 155 | 1.1854
[8 empty] | 123 | 0.05521 | 123 | 0.07858 | 125 | 0.08324 | 125 | 0.11364 | 129 | 0.14924 | 129 | 0.19334 | 133 | 0.26205 | 133 | 0.32913 | 140 | 0.39948 | 140 | 0.49884 | 147 | 0.64006 | 147 | 0.79749 | 156 | 0.9376 | 156 | 1.1691
[8 empty] | 124 | 0.05439 | 124 | 0.07751 | 126 | 0.08204 | 126 | 0.11202 | 130 | 0.14713 | 130 | 0.19051 | 134 | 0.25842 | 134 | 0.3243 | 141 | 0.39417 | 141 | 0.49168 | 148 | 0.63185 | 148 | 0.7863 | 157 | 0.92605 | 157 | 1.1532
[8 empty] | 125 | 0.05282 | 125 | 0.07646 | 127 | 0.08086 | 127 | 0.11043 | 131 | 0.14507 | 131 | 0.18776 | 135 | 0.25487 | 135 | 0.31958 | 142 | 0.38897 | 142 | 0.48468 | 149 | 0.62381 | 149 | 0.77534 | 158 | 0.91472 | 158 | 1.1376
[8 empty] | 126 | 0.05206 | 126 | 0.07543 | 128 | 0.07971 | 128 | 0.10889 | 132 | 0.14305 | 132 | 0.18506 | 136 | 0.24799 | 136 | 0.31496 | 143 | 0.38387 | 143 | 0.47783 | 150 | 0.61592 | 150 | 0.76462 | 159 | 0.9036 | 159 | 1.1223
[8 empty] | 127 | 0.05131 | 127 | 0.07443 | 129 | 0.07859 | 129 | 0.10738 | 133 | 0.14107 | 133 | 0.18243 | 137 | 0.24465 | 137 | 0.31045 | 144 | 0.37887 | 144 | 0.47113 | 151 | 0.60818 | 151 | 0.75413 | 160 | 0.89268 | 160 | 1.1073
[8 empty] | 128 | 0.05058 | 128 | 0.07345 | 130 | 0.07748 | 130 | 0.1059 | 134 | 0.13913 | 134 | 0.17986 | 138 | 0.24138 | 138 | 0.30604 | 145 | 0.36916 | 145 | 0.46458 | 152 | 0.60059 | 152 | 0.74386 | 161 | 0.88197 | 161 | 1.0927
[8 empty] | 129 | 0.04987 | 129 | 0.0725 | 131 | 0.0764 | 131 | 0.10446 | 135 | 0.13724 | 135 | 0.17735 | 139 | 0.23818 | 139 | 0.30173 | 146 | 0.36445 | 146 | 0.45816 | 153 | 0.59314 | 153 | 0.7338 | 162 | 0.87145 | 162 | 1.0783
[8 empty] | 130 | 0.04917 | 130 | 0.07156 | 132 | 0.07534 | 132 | 0.10305 | 136 | 0.13356 | 136 | 0.17489 | 140 | 0.23504 | 140 | 0.29751 | 147 | 0.35982 | 147 | 0.45189 | 154 | 0.58583 | 154 | 0.72395 | 163 | 0.86112 | 163 | 1.0643
[8 empty] | 131 | 0.04849 | 131 | 0.07065 | 133 | 0.07431 | 133 | 0.10168 | 137 | 0.13178 | 137 | 0.17249 | 141 | 0.23196 | 141 | 0.29339 | 148 | 0.35529 | 148 | 0.44575 | 155 | 0.57866 | 155 | 0.71431 | 164 | 0.85098 | 164 | 1.0505
[8 empty] | 132 | 0.04782 | 132 | 0.06976 | 134 | 0.07329 | 134 | 0.10033 | 138 | 0.13003 | 138 | 0.17014 | 142 | 0.22894 | 142 | 0.28935 | 149 | 0.35084 | 149 | 0.43973 | 156 | 0.56471 | 156 | 0.70487 | 165 | 0.83124 | 165 | 1.037
[8 empty] | 133 | 0.04716 | 133 | 0.06889 | 135 | 0.0723 | 135 | 0.09902 | 139 | 0.12831 | 139 | 0.16784 | 143 | 0.22598 | 143 | 0.2854 | 150 | 0.34648 | 150 | 0.43384 | 157 | 0.55793 | 157 | 0.69561 | 166 | 0.82163 | 166 | 1.0238
[8 empty] | 134 | 0.04652 | 134 | 0.06804 | 136 | 0.07037 | 136 | 0.09773 | 140 | 0.12663 | 140 | 0.16559 | 144 | 0.22308 | 144 | 0.28154 | 151 | 0.34219 | 151 | 0.42808 | 158 | 0.55127 | 158 | 0.68655 | 167 | 0.81219 | 167 | 1.0108
[8 empty] | 135 | 0.04589 | 135 | 0.06721 | 137 | 0.06944 | 137 | 0.09647 | 141 | 0.12499 | 141 | 0.16339 | 145 | 0.21744 | 145 | 0.27775 | 152 | 0.33799 | 152 | 0.42243 | 159 | 0.54472 | 159 | 0.67766 | 168 | 0.80291 | 168 | 0.99807
[8 empty] | 136 | 0.04467 | 136 | 0.06639 | 138 | 0.06852 | 138 | 0.09524 | 142 | 0.12337 | 142 | 0.16124 | 146 | 0.21471 | 146 | 0.27405 | 153 | 0.33387 | 153 | 0.4169 | 160 | 0.5383 | 160 | 0.66896 | 169 | 0.79379 | 169 | 0.9856
[8 empty] | 137 | 0.04408 | 137 | 0.0656 | 139 | 0.06762 | 139 | 0.09404 | 143 | 0.12179 | 143 | 0.15913 | 147 | 0.21202 | 147 | 0.27042 | 154 | 0.32982 | 154 | 0.41148 | 161 | 0.53199 | 161 | 0.66042 | 170 | 0.78483 | 170 | 0.97337
[8 empty] | 138 | 0.04349 | 138 | 0.06482 | 140 | 0.06674 | 140 | 0.09286 | 144 | 0.12024 | 144 | 0.15707 | 148 | 0.20938 | 148 | 0.26687 | 155 | 0.32584 | 155 | 0.40617 | 162 | 0.52579 | 162 | 0.65206 | 171 | 0.77603 | 171 | 0.96137
[8 empty] | 139 | 0.04293 | 139 | 0.06406 | 141 | 0.06587 | 141 | 0.09171 | 145 | 0.11722 | 145 | 0.15505 | 149 | 0.2068 | 149 | 0.2634 | 156 | 0.3181 | 156 | 0.40097 | 163 | 0.51971 | 163 | 0.64385 | 172 | 0.76737 | 172 | 0.9496
[8 empty] | 140 | 0.04237 | 140 | 0.06331 | 142 | 0.06503 | 142 | 0.09059 | 146 | 0.11575 | 146 | 0.15307 | 150 | 0.20426 | 150 | 0.25999 | 157 | 0.31434 | 157 | 0.39587 | 164 | 0.51372 | 164 | 0.63581 | 173 | 0.75887 | 173 | 0.93805
[8 empty] | 141 | 0.04182 | 141 | 0.06258 | 143 | 0.0642 | 143 | 0.08948 | 147 | 0.11431 | 147 | 0.15113 | 151 | 0.20176 | 151 | 0.25665 | 158 | 0.31064 | 158 | 0.39087 | 165 | 0.50207 | 165 | 0.62792 | 174 | 0.7505 | 174 | 0.92672
[8 empty] | 142 | 0.04128 | 142 | 0.06187 | 144 | 0.06338 | 144 | 0.0884 | 148 | 0.1129 | 148 | 0.14924 | 152 | 0.19932 | 152 | 0.25338 | 159 | 0.30701 | 159 | 0.38597 | 166 | 0.49639 | 166 | 0.62018 | 175 | 0.73419 | 175 | 0.9156
[8 empty] | 143 | 0.04076 | 143 | 0.06117 | 145 | 0.0618 | 145 | 0.08734 | 149 | 0.11151 | 149 | 0.14738 | 153 | 0.19691 | 153 | 0.25018 | 160 | 0.30344 | 160 | 0.38116 | 167 | 0.49081 | 167 | 0.61259 | 176 | 0.72623 | 176 | 0.90468
[8 empty] | 144 | 0.04024 | 144 | 0.06049 | 146 | 0.06103 | 146 | 0.08631 | 150 | 0.11015 | 150 | 0.14556 | 154 | 0.19455 | 154 | 0.24704 | 161 | 0.29993 | 161 | 0.37645 | 168 | 0.48532 | 168 | 0.60514 | 177 | 0.71841 | 177 | 0.89397
[8 empty] | 145 | 0.03924 | 145 | 0.05982 | 147 | 0.06027 | 147 | 0.08529 | 151 | 0.10882 | 151 | 0.14378 | 155 | 0.19224 | 155 | 0.24396 | 162 | 0.29649 | 162 | 0.37182 | 169 | 0.47993 | 169 | 0.59783 | 178 | 0.71071 | 178 | 0.88345
[8 empty] | 146 | 0.03875 | 146 | 0.05916 | 148 | 0.05953 | 148 | 0.0843 | 152 | 0.10751 | 152 | 0.14203 | 156 | 0.18773 | 156 | 0.24094 | 163 | 0.2931 | 163 | 0.36729 | 170 | 0.47463 | 170 | 0.59066 | 179 | 0.70314 | 179 | 0.87312
[8 empty] | 147 | 0.03827 | 147 | 0.05852 | 149 | 0.0588 | 149 | 0.08332 | 153 | 0.10622 | 153 | 0.14031 | 157 | 0.18553 | 157 | 0.23798 | 164 | 0.28977 | 164 | 0.36284 | 171 | 0.46941 | 171 | 0.58362 | 180 | 0.69569 | 180 | 0.86298
[8 empty] | 148 | 0.0378 | 148 | 0.05789 | 150 | 0.05809 | 150 | 0.08237 | 154 | 0.10495 | 154 | 0.13863 | 158 | 0.18337 | 158 | 0.23508 | 165 | 0.28329 | 165 | 0.35848 | 172 | 0.46429 | 172 | 0.57671 | 181 | 0.68836 | 181 | 0.85302
[8 empty] | 149 | 0.03734 | 149 | 0.05727 | 151 | 0.05739 | 151 | 0.08144 | 155 | 0.10371 | 155 | 0.13699 | 159 | 0.18125 | 159 | 0.23224 | 166 | 0.28013 | 166 | 0.35419 | 173 | 0.45924 | 173 | 0.56993 | 182 | 0.68115 | 182 | 0.84324
[8 empty] | 150 | 0.03689 | 150 | 0.05667 | 152 | 0.0567 | 152 | 0.08052 | 156 | 0.10129 | 156 | 0.13537 | 160 | 0.17917 | 160 | 0.22944 | 167 | 0.27702 | 167 | 0.34999 | 174 | 0.45428 | 174 | 0.56327 | 183 | 0.67405 | 183 | 0.83363
[8 empty] | 151 | 0.03644 | 151 | 0.05608 | 153 | 0.05602 | 153 | 0.07962 | 157 | 0.10011 | 157 | 0.13379 | 161 | 0.17712 | 161 | 0.22671 | 168 | 0.27396 | 168 | 0.34587 | 175 | 0.4446 | 175 | 0.55672 | 184 | 0.66707 | 184 | 0.82419
[8 empty] | 152 | 0.036 | 152 | 0.05549 | 154 | 0.05536 | 154 | 0.07874 | 158 | 0.09896 | 158 | 0.13224 | 162 | 0.17511 | 162 | 0.22402 | 169 | 0.27096 | 169 | 0.34182 | 176 | 0.43988 | 176 | 0.5503 | 185 | 0.65342 | 185 | 0.81491
[8 empty] | 153 | 0.03557 | 153 | 0.05493 | 155 | 0.0547 | 155 | 0.07787 | 159 | 0.09782 | 159 | 0.13071 | 163 | 0.17313 | 163 | 0.22138 | 170 | 0.268 | 170 | 0.33784 | 177 | 0.43523 | 177 | 0.54399 | 186 | 0.64676 | 186 | 0.80579
[8 empty] | 154 | 0.03515 | 154 | 0.05437 | 156 | 0.05343 | 156 | 0.07703 | 160 | 0.0967 | 160 | 0.12922 | 164 | 0.17119 | 164 | 0.2188 | 171 | 0.26509 | 171 | 0.33394 | 178 | 0.43065 | 178 | 0.53779 | 187 | 0.6402 | 187 | 0.79683
[8 empty] | 155 | 0.03474 | 155 | 0.05382 | 157 | 0.05281 | 157 | 0.0762 | 161 | 0.0956 | 161 | 0.12775 | 165 | 0.1674 | 165 | 0.21626 | 172 | 0.26223 | 172 | 0.3301 | 179 | 0.42615 | 179 | 0.53171 | 188 | 0.63374 | 188 | 0.78803
[8 empty] | 156 | 0.03393 | 156 | 0.05328 | 158 | 0.0522 | 158 | 0.07538 | 162 | 0.09452 | 162 | 0.12631 | 166 | 0.16555 | 166 | 0.21376 | 173 | 0.25942 | 173 | 0.32634 | 180 | 0.42172 | 180 | 0.52572 | 189 | 0.62738 | 189 | 0.77937
[8 empty] | 157 | 0.03354 | 157 | 0.05276 | 159 | 0.05161 | 159 | 0.07458 | 163 | 0.09346 | 163 | 0.1249 | 167 | 0.16373 | 167 | 0.21132 | 174 | 0.25665 | 174 | 0.32264 | 181 | 0.41736 | 181 | 0.51985 | 190 | 0.62111 | 190 | 0.77087
[8 empty] | 158 | 0.03316 | 158 | 0.05224 | 160 | 0.05102 | 160 | 0.0738 | 164 | 0.09242 | 164 | 0.12351 | 168 | 0.16194 | 168 | 0.20891 | 175 | 0.25125 | 175 | 0.31901 | 182 | 0.41307 | 182 | 0.51407 | 191 | 0.61494 | 191 | 0.7625
[8 empty] | 159 | 0.015625 | 159 | 0.05173 | 161 | 0.05044 | 161 | 0.07303 | 165 | 0.09038 | 165 | 0.12215 | 169 | 0.16019 | 169 | 0.20655 | 176 | 0.24861 | 176 | 0.31544 | 183 | 0.40884 | 183 | 0.50839 | 192 | 0.60887 | 192 | 0.75428
[8 empty] | 160 | 0.015625 | 160 | 0.05124 | 162 | 0.04987 | 162 | 0.07227 | 166 | 0.08939 | 166 | 0.12082 | 170 | 0.15846 | 170 | 0.20424 | 177 | 0.24601 | 177 | 0.31193 | 184 | 0.40468 | 184 | 0.50281 | 193 | 0.60288 | 193 | 0.74619
[8 empty] | 161 | 0.015625 | 161 | 0.05075 | 163 | 0.04931 | 163 | 0.07153 | 167 | 0.08841 | 167 | 0.11951 | 171 | 0.15675 | 171 | 0.20196 | 178 | 0.24346 | 178 | 0.30849 | 185 | 0.39655 | 185 | 0.49732 | 194 | 0.59698 | 194 | 0.73823
[8 empty] | 162 | 0.015625 | 162 | 0.05027 | 164 | 0.04877 | 164 | 0.0708 | 168 | 0.08745 | 168 | 0.11822 | 172 | 0.15508 | 172 | 0.19973 | 179 | 0.24094 | 179 | 0.3051 | 186 | 0.39257 | 186 | 0.49193 | 195 | 0.58545 | 195 | 0.73041
[8 empty] | 163 | 0.015625 | 163 | 0.0498 | 165 | 0.0477 | 165 | 0.07009 | 169 | 0.08651 | 169 | 0.11695 | 173 | 0.15343 | 173 | 0.19753 | 180 | 0.23846 | 180 | 0.30177 | 187 | 0.38866 | 187 | 0.48663 | 196 | 0.57981 | 196 | 0.72271
[8 empty] | 164 | 0.015625 | 164 | 0.04934 | 166 | 0.04717 | 166 | 0.06939 | 170 | 0.08558 | 170 | 0.11571 | 174 | 0.15181 | 174 | 0.19537 | 181 | 0.23603 | 181 | 0.2985 | 188 | 0.3848 | 188 | 0.48141 | 197 | 0.57425 | 197 | 0.71514
[8 empty] | 165 | 0.015625 | 165 | 0.04889 | 167 | 0.04666 | 167 | 0.0687 | 171 | 0.08466 | 171 | 0.11449 | 175 | 0.14864 | 175 | 0.19325 | 182 | 0.23362 | 182 | 0.29529 | 189 | 0.38101 | 189 | 0.47629 | 198 | 0.56877 | 198 | 0.70769
[8 empty] | 166 | 0.015625 | 166 | 0.04844 | 168 | 0.04615 | 168 | 0.06802 | 172 | 0.08376 | 172 | 0.11329 | 176 | 0.1471 | 176 | 0.19117 | 183 | 0.23126 | 183 | 0.29213 | 190 | 0.37727 | 190 | 0.47124 | 199 | 0.56338 | 199 | 0.70036
[8 empty] | 167 | 0.015625 | 167 | 0.048 | 169 | 0.04566 | 169 | 0.06736 | 173 | 0.08287 | 173 | 0.11211 | 177 | 0.14557 | 177 | 0.18912 | 184 | 0.22893 | 184 | 0.28902 | 191 | 0.37358 | 191 | 0.46628 | 200 | 0.55805 | 200 | 0.69315
[8 empty] | 168 | 0.015625 | 168 | 0.04757 | 170 | 0.04517 | 170 | 0.0667 | 174 | 0.082 | 174 | 0.11096 | 178 | 0.14408 | 178 | 0.18711 | 185 | 0.22438 | 185 | 0.28596 | 192 | 0.36995 | 192 | 0.4614 | 201 | 0.55281 | 201 | 0.68605
[8 empty] | 169 | 0.015625 | 169 | 0.04715 | 171 | 0.04469 | 171 | 0.06606 | 175 | 0.0803 | 175 | 0.10982 | 179 | 0.1426 | 179 | 0.18513 | 186 | 0.22215 | 186 | 0.28296 | 193 | 0.36637 | 193 | 0.4566 | 202 | 0.54764 | 202 | 0.67907
[8 empty] | 170 | 0.015625 | 170 | 0.04674 | 172 | 0.04421 | 172 | 0.06543 | 176 | 0.07947 | 176 | 0.1087 | 180 | 0.14115 | 180 | 0.18319 | 187 | 0.21996 | 187 | 0.28 | 194 | 0.36285 | 194 | 0.45188 | 203 | 0.54254 | 203 | 0.67219
[8 empty] | 171 | 0.015625 | 171 | 0.04633 | 173 | 0.04375 | 173 | 0.06481 | 177 | 0.07865 | 177 | 0.1076 | 181 | 0.13972 | 181 | 0.18128 | 188 | 0.2178 | 188 | 0.27709 | 195 | 0.35595 | 195 | 0.44723 | 204 | 0.53752 | 204 | 0.66542
[8 empty] | 172 | 0.015625 | 172 | 0.04593 | 174 | 0.04329 | 174 | 0.0642 | 178 | 0.07784 | 178 | 0.10652 | 182 | 0.13831 | 182 | 0.1794 | 189 | 0.21568 | 189 | 0.27423 | 196 | 0.35257 | 196 | 0.44265 | 205 | 0.52768 | 205 | 0.65876
[8 empty] | 173 | 0.015625 | 173 | 0.04554 | 175 | 0.04239 | 175 | 0.06361 | 179 | 0.07705 | 179 | 0.10546 | 183 | 0.13692 | 183 | 0.17755 | 190 | 0.21358 | 190 | 0.27142 | 197 | 0.34924 | 197 | 0.43815 | 206 | 0.52286 | 206 | 0.6522
[8 empty] | 174 | 0.015625 | 174 | 0.04516 | 176 | 0.04195 | 176 | 0.06302 | 180 | 0.07627 | 180 | 0.10442 | 184 | 0.13555 | 184 | 0.17573 | 191 | 0.21151 | 191 | 0.26865 | 198 | 0.34596 | 198 | 0.43372 | 207 | 0.51811 | 207 | 0.64574
[8 empty] | 175 | 0.015625 | 175 | 0.03334 | 177 | 0.04152 | 177 | 0.06244 | 181 | 0.0755 | 181 | 0.10339 | 185 | 0.13288 | 185 | 0.17394 | 192 | 0.20948 | 192 | 0.26593 | 199 | 0.34273 | 199 | 0.42936 | 208 | 0.51342 | 208 | 0.63938
[8 empty] | 453 | 0.015625 | 453 | 0.03334 | 178 | 0.0411 | 178 | 0.06187 | 182 | 0.07474 | 182 | 0.10238 | 186 | 0.13157 | 186 | 0.17219 | 193 | 0.20747 | 193 | 0.26325 | 200 | 0.33954 | 200 | 0.42507 | 209 | 0.5088 | 209 | 0.63311
[8 empty] | 454 | 0.011042 | 454 | 0.03334 | 179 | 0.04068 | 179 | 0.06131 | 183 | 0.07399 | 183 | 0.10139 | 187 | 0.13029 | 187 | 0.17046 | 194 | 0.20549 | 194 | 0.26061 | 201 | 0.3364 | 201 | 0.42084 | 210 | 0.50424 | 210 | 0.62694
[8 empty] | 455 | 0.001 | 455 | 0.03334 | 180 | 0.04027 | 180 | 0.06077 | 184 | 0.07326 | 184 | 0.10041 | 188 | 0.12902 | 188 | 0.16875 | 195 | 0.20162 | 195 | 0.25801 | 202 | 0.3333 | 202 | 0.41668 | 211 | 0.49974 | 211 | 0.62087
[8 empty] | 500 | 0.001 | 500 | 0.03334 | 181 | 0.03986 | 181 | 0.06023 | 185 | 0.07182 | 185 | 0.09945 | 189 | 0.12777 | 189 | 0.16708 | 196 | 0.19973 | 196 | 0.25546 | 203 | 0.33024 | 203 | 0.41258 | 212 | 0.4953 | 212 | 0.61488
[8 empty] | 501 | 0.001 | 501 | 0.01667 | 182 | 0.03946 | 182 | 0.0597 | 186 | 0.07112 | 186 | 0.09851 | 190 | 0.12654 | 190 | 0.16543 | 197 | 0.19786 | 197 | 0.25294 | 204 | 0.32722 | 204 | 0.40855 | 213 | 0.49092 | 213 | 0.60898
[8 empty] | 6300 | 0.001 | 6300 | 0.01667 | 183 | 0.03907 | 183 | 0.05917 | 187 | 0.07042 | 187 | 0.09758 | 191 | 0.12532 | 191 | 0.16381 | 198 | 0.19602 | 198 | 0.25046 | 205 | 0.32132 | 205 | 0.40457 | 214 | 0.4866 | 214 | 0.60317
[12 empty] | 184 | 0.03868 | 184 | 0.05866 | 188 | 0.06974 | 188 | 0.09666 | 192 | 0.12413 | 192 | 0.16221 | 199 | 0.19421 | 199 | 0.24803 | 206 | 0.31842 | 206 | 0.40066 | 215 | 0.47814 | 215 | 0.59745
[12 empty] | 185 | 0.03793 | 185 | 0.05815 | 189 | 0.06907 | 189 | 0.09576 | 193 | 0.12295 | 193 | 0.16064 | 200 | 0.19242 | 200 | 0.24562 | 207 | 0.31557 | 207 | 0.3968 | 216 | 0.47399 | 216 | 0.59181
[12 empty] | 186 | 0.03756 | 186 | 0.05766 | 190 | 0.0684 | 190 | 0.09487 | 194 | 0.12178 | 194 | 0.1591 | 201 | 0.19065 | 201 | 0.24326 | 208 | 0.31276 | 208 | 0.39301 | 217 | 0.46989 | 217 | 0.58625
[12 empty] | 187 | 0.03719 | 187 | 0.05717 | 191 | 0.06775 | 191 | 0.094 | 195 | 0.11951 | 195 | 0.15757 | 202 | 0.18891 | 202 | 0.24093 | 209 | 0.30998 | 209 | 0.38927 | 218 | 0.46585 | 218 | 0.58077
[12 empty] | 188 | 0.03683 | 188 | 0.05669 | 192 | 0.06711 | 192 | 0.09314 | 196 | 0.11839 | 196 | 0.15608 | 203 | 0.18719 | 203 | 0.23864 | 210 | 0.30724 | 210 | 0.38558 | 219 | 0.46186 | 219 | 0.57538
[12 empty] | 189 | 0.03648 | 189 | 0.05621 | 193 | 0.06647 | 193 | 0.0923 | 197 | 0.11729 | 197 | 0.1546 | 204 | 0.1855 | 204 | 0.23638 | 211 | 0.30454 | 211 | 0.38195 | 220 | 0.45792 | 220 | 0.57005
[12 empty] | 190 | 0.03613 | 190 | 0.05575 | 194 | 0.06584 | 194 | 0.09147 | 198 | 0.11621 | 198 | 0.15315 | 205 | 0.18218 | 205 | 0.23415 | 212 | 0.30187 | 212 | 0.37837 | 221 | 0.45403 | 221 | 0.56481
[12 empty] | 191 | 0.03578 | 191 | 0.05529 | 195 | 0.06462 | 195 | 0.09065 | 199 | 0.11514 | 199 | 0.15172 | 206 | 0.18055 | 206 | 0.23196 | 213 | 0.29923 | 213 | 0.37485 | 222 | 0.4502 | 222 | 0.55964
[12 empty] | 192 | 0.03544 | 192 | 0.05484 | 196 | 0.06402 | 196 | 0.08984 | 200 | 0.11409 | 200 | 0.15031 | 207 | 0.17895 | 207 | 0.2298 | 214 | 0.29664 | 214 | 0.37137 | 223 | 0.44641 | 223 | 0.55454
[12 empty] | 193 | 0.03511 | 193 | 0.05439 | 197 | 0.06343 | 197 | 0.08905 | 201 | 0.11305 | 201 | 0.14892 | 208 | 0.17736 | 208 | 0.22768 | 215 | 0.29154 | 215 | 0.36795 | 224 | 0.44267 | 224 | 0.54952
[12 empty] | 194 | 0.03478 | 194 | 0.05395 | 198 | 0.06284 | 198 | 0.08827 | 202 | 0.11202 | 202 | 0.14755 | 209 | 0.1758 | 209 | 0.22558 | 216 | 0.28904 | 216 | 0.36457 | 225 | 0.43533 | 225 | 0.54456
[12 empty] | 195 | 0.03413 | 195 | 0.05352 | 199 | 0.06227 | 199 | 0.0875 | 203 | 0.11101 | 203 | 0.14621 | 210 | 0.17426 | 210 | 0.22351 | 217 | 0.28658 | 217 | 0.36124 | 226 | 0.43173 | 226 | 0.53968
[12 empty] | 196 | 0.03382 | 196 | 0.0531 | 200 | 0.0617 | 200 | 0.08674 | 204 | 0.11001 | 204 | 0.14488 | 211 | 0.17274 | 211 | 0.22148 | 218 | 0.28414 | 218 | 0.35796 | 227 | 0.42817 | 227 | 0.53486
[12 empty] | 197 | 0.0335 | 197 | 0.05268 | 201 | 0.06114 | 201 | 0.08599 | 205 | 0.10806 | 205 | 0.14357 | 212 | 0.17124 | 212 | 0.21947 | 219 | 0.28174 | 219 | 0.35473 | 228 | 0.42466 | 228 | 0.53011
[12 empty] | 198 | 0.0332 | 198 | 0.05227 | 202 | 0.06059 | 202 | 0.08526 | 206 | 0.1071 | 206 | 0.14229 | 213 | 0.16976 | 213 | 0.21749 | 220 | 0.27937 | 220 | 0.35154 | 229 | 0.42119 | 229 | 0.52542
[12 empty] | 199 | 0.015625 | 199 | 0.05186 | 203 | 0.06004 | 203 | 0.08453 | 207 | 0.10616 | 207 | 0.14102 | 214 | 0.1683 | 214 | 0.21555 | 221 | 0.27702 | 221 | 0.3484 | 230 | 0.41776 | 230 | 0.5208
[12 empty] | 200 | 0.015625 | 200 | 0.05146 | 204 | 0.0595 | 204 | 0.08382 | 208 | 0.10522 | 208 | 0.13977 | 215 | 0.16543 | 215 | 0.21362 | 222 | 0.27471 | 222 | 0.3453 | 231 | 0.41438 | 231 | 0.51624
[12 empty] | 201 | 0.015625 | 201 | 0.05107 | 205 | 0.05845 | 205 | 0.08312 | 209 | 0.1043 | 209 | 0.13854 | 216 | 0.16402 | 216 | 0.21173 | 223 | 0.27243 | 223 | 0.34224 | 232 | 0.41104 | 232 | 0.51174
[12 empty] | 202 | 0.015625 | 202 | 0.05068 | 206 | 0.05793 | 206 | 0.08242 | 210 | 0.10339 | 210 | 0.13732 | 217 | 0.16263 | 217 | 0.20986 | 224 | 0.27017 | 224 | 0.33922 | 233 | 0.40774 | 233 | 0.5073
[12 empty] | 203 | 0.015625 | 203 | 0.0503 | 207 | 0.05742 | 207 | 0.08174 | 211 | 0.1025 | 211 | 0.13613 | 218 | 0.16126 | 218 | 0.20802 | 225 | 0.26574 | 225 | 0.33625 | 234 | 0.40448 | 234 | 0.50292
[12 empty] | 204 | 0.015625 | 204 | 0.04993 | 208 | 0.05692 | 208 | 0.08107 | 212 | 0.10161 | 212 | 0.13495 | 219 | 0.15991 | 219 | 0.20621 | 226 | 0.26357 | 226 | 0.33332 | 235 | 0.40125 | 235 | 0.4986
[12 empty] | 205 | 0.015625 | 205 | 0.04956 | 209 | 0.05642 | 209 | 0.0804 | 213 | 0.10074 | 213 | 0.13378 | 220 | 0.15857 | 220 | 0.20442 | 227 | 0.26143 | 227 | 0.33042 | 236 | 0.39492 | 236 | 0.49434
[12 empty] | 206 | 0.015625 | 206 | 0.04919 | 210 | 0.05593 | 210 | 0.07975 | 214 | 0.09988 | 214 | 0.13264 | 221 | 0.15725 | 221 | 0.20265 | 228 | 0.25931 | 228 | 0.32757 | 237 | 0.39182 | 237 | 0.49014
[12 empty] | 207 | 0.015625 | 207 | 0.04883 | 211 | 0.05545 | 211 | 0.07911 | 215 | 0.09819 | 215 | 0.13151 | 222 | 0.15595 | 222 | 0.20091 | 229 | 0.25721 | 229 | 0.32476 | 238 | 0.38874 | 238 | 0.48599
[12 empty] | 208 | 0.015625 | 208 | 0.04848 | 212 | 0.05497 | 212 | 0.07847 | 216 | 0.09736 | 216 | 0.13039 | 223 | 0.15466 | 223 | 0.19919 | 230 | 0.25514 | 230 | 0.32198 | 239 | 0.38571 | 239 | 0.48189
[12 empty] | 209 | 0.015625 | 209 | 0.04813 | 213 | 0.0545 | 213 | 0.07784 | 217 | 0.09654 | 217 | 0.12929 | 224 | 0.15339 | 224 | 0.1975 | 231 | 0.2531 | 231 | 0.31924 | 240 | 0.38271 | 240 | 0.47785
[12 empty] | 210 | 0.015625 | 210 | 0.04778 | 214 | 0.05404 | 214 | 0.07723 | 218 | 0.09573 | 218 | 0.12821 | 225 | 0.15089 | 225 | 0.19583 | 232 | 0.25108 | 232 | 0.31654 | 241 | 0.37975 | 241 | 0.47386
[12 empty] | 211 | 0.015625 | 211 | 0.04744 | 215 | 0.05312 | 215 | 0.07662 | 219 | 0.09493 | 219 | 0.12714 | 226 | 0.14967 | 226 | 0.19418 | 233 | 0.24909 | 233 | 0.31387 | 242 | 0.37682 | 242 | 0.46992
[12 empty] | 212 | 0.015625 | 212 | 0.04711 | 216 | 0.05268 | 216 | 0.07602 | 220 | 0.09414 | 220 | 0.12609 | 227 | 0.14846 | 227 | 0.19255 | 234 | 0.24712 | 234 | 0.31123 | 243 | 0.37392 | 243 | 0.46603
[12 empty] | 213 | 0.015625 | 213 | 0.04678 | 217 | 0.05224 | 217 | 0.07543 | 221 | 0.09336 | 221 | 0.12505 | 228 | 0.14726 | 228 | 0.19095 | 235 | 0.24517 | 235 | 0.30864 | 244 | 0.37106 | 244 | 0.4622
[12 empty] | 214 | 0.015625 | 214 | 0.04645 | 218 | 0.0518 | 218 | 0.07484 | 222 | 0.09259 | 222 | 0.12402 | 229 | 0.14608 | 229 | 0.18936 | 236 | 0.24134 | 236 | 0.30607 | 245 | 0.36544 | 245 | 0.45841
[12 empty] | 215 | 0.015625 | 215 | 0.04613 | 219 | 0.05137 | 219 | 0.07427 | 223 | 0.09183 | 223 | 0.12301 | 230 | 0.14492 | 230 | 0.1878 | 237 | 0.23946 | 237 | 0.30354 | 246 | 0.36267 | 246 | 0.45467
[12 empty] | 216 | 0.015625 | 216 | 0.04582 | 220 | 0.05094 | 220 | 0.0737 | 224 | 0.09108 | 224 | 0.12201 | 231 | 0.14376 | 231 | 0.18626 | 238 | 0.23761 | 238 | 0.30104 | 247 | 0.35994 | 247 | 0.45097
[12 empty] | 217 | 0.015625 | 217 | 0.0455 | 221 | 0.05052 | 221 | 0.07314 | 225 | 0.08961 | 225 | 0.12103 | 232 | 0.14262 | 232 | 0.18474 | 239 | 0.23577 | 239 | 0.29858 | 248 | 0.35724 | 248 | 0.44733
[12 empty] | 218 | 0.015625 | 218 | 0.0452 | 222 | 0.05011 | 222 | 0.07259 | 226 | 0.08888 | 226 | 0.12006 | 233 | 0.1415 | 233 | 0.18324 | 240 | 0.23396 | 240 | 0.29614 | 249 | 0.35457 | 249 | 0.44373
[12 empty] | 219 | 0.015625 | 219 | 0.03334 | 223 | 0.0497 | 223 | 0.07204 | 227 | 0.08817 | 227 | 0.1191 | 234 | 0.14039 | 234 | 0.18176 | 241 | 0.23216 | 241 | 0.29374 | 250 | 0.35193 | 250 | 0.44017
[12 empty] | 453 | 0.015625 | 453 | 0.03334 | 224 | 0.04929 | 224 | 0.0715 | 228 | 0.08746 | 228 | 0.11816 | 235 | 0.13929 | 235 | 0.1803 | 242 | 0.23039 | 242 | 0.29137 | 251 | 0.34931 | 251 | 0.43666
[12 empty] | 454 | 0.011042 | 454 | 0.03334 | 225 | 0.0485 | 225 | 0.07097 | 229 | 0.08677 | 229 | 0.11722 | 236 | 0.13713 | 236 | 0.17885 | 243 | 0.22864 | 243 | 0.28902 | 252 | 0.34673 | 252 | 0.43319
[12 empty] | 455 | 0.001 | 455 | 0.03334 | 226 | 0.04811 | 226 | 0.07045 | 230 | 0.08608 | 230 | 0.1163 | 237 | 0.13607 | 237 | 0.17743 | 244 | 0.22691 | 244 | 0.28671 | 253 | 0.34418 | 253 | 0.42976
[12 empty] | 500 | 0.001 | 500 | 0.03334 | 227 | 0.04772 | 227 | 0.06993 | 231 | 0.0854 | 231 | 0.11539 | 238 | 0.13502 | 238 | 0.17602 | 245 | 0.2235 | 245 | 0.28443 | 254 | 0.34165 | 254 | 0.42638
[12 empty] | 501 | 0.001 | 501 | 0.01667 | 228 | 0.04734 | 228 | 0.06942 | 232 | 0.08472 | 232 | 0.1145 | 239 | 0.13398 | 239 | 0.17463 | 246 | 0.22183 | 246 | 0.28217 | 255 | 0.33916 | 255 | 0.42304
[12 empty] | 6300 | 0.001 | 6300 | 0.01667 | 229 | 0.04696 | 229 | 0.06892 | 233 | 0.08406 | 233 | 0.11361 | 240 | 0.13296 | 240 | 0.17326 | 247 | 0.22017 | 247 | 0.27994 | 256 | 0.33424 | 256 | 0.41974
[16 empty] | 230 | 0.04659 | 230 | 0.06842 | 234 | 0.0834 | 234 | 0.11274 | 241 | 0.13195 | 241 | 0.17191 | 248 | 0.21853 | 248 | 0.27774 | 257 | 0.33183 | 257 | 0.41648
[16 empty] | 231 | 0.04622 | 231 | 0.06793 | 235 | 0.08275 | 235 | 0.11188 | 242 | 0.13094 | 242 | 0.17057 | 249 | 0.21692 | 249 | 0.27557 | 258 | 0.32944 | 258 | 0.41325
[16 empty] | 232 | 0.04586 | 232 | 0.06745 | 236 | 0.08148 | 236 | 0.11103 | 243 | 0.12995 | 243 | 0.16925 | 250 | 0.21532 | 250 | 0.27343 | 259 | 0.32708 | 259 | 0.41007
[16 empty] | 233 | 0.0455 | 233 | 0.06697 | 237 | 0.08085 | 237 | 0.11019 | 244 | 0.12898 | 244 | 0.16795 | 251 | 0.21373 | 251 | 0.27131 | 260 | 0.32474 | 260 | 0.40692
[16 empty] | 234 | 0.04515 | 234 | 0.0665 | 238 | 0.08023 | 238 | 0.10936 | 245 | 0.12705 | 245 | 0.16666 | 252 | 0.21217 | 252 | 0.26921 | 261 | 0.32242 | 261 | 0.40382
[16 empty] | 235 | 0.0448 | 235 | 0.06604 | 239 | 0.07962 | 239 | 0.10854 | 246 | 0.12611 | 246 | 0.16539 | 253 | 0.21062 | 253 | 0.26714 | 262 | 0.32014 | 262 | 0.40074
[16 empty] | 236 | 0.04411 | 236 | 0.06558 | 240 | 0.07901 | 240 | 0.10773 | 247 | 0.12517 | 247 | 0.16413 | 254 | 0.20909 | 254 | 0.2651 | 263 | 0.31787 | 263 | 0.39771
[16 empty] | 237 | 0.04377 | 237 | 0.06512 | 241 | 0.07841 | 241 | 0.10693 | 248 | 0.12424 | 248 | 0.16289 | 255 | 0.20757 | 255 | 0.26308 | 264 | 0.31563 | 264 | 0.39471
[16 empty] | 238 | 0.04343 | 238 | 0.06468 | 242 | 0.07782 | 242 | 0.10614 | 249 | 0.12333 | 249 | 0.16167 | 256 | 0.2046 | 256 | 0.26109 | 265 | 0.31123 | 265 | 0.39175
[16 empty] | 239 | 0.0431 | 239 | 0.06424 | 243 | 0.07723 | 243 | 0.10536 | 250 | 0.12243 | 250 | 0.16046 | 257 | 0.20313 | 257 | 0.25912 | 266 | 0.30906 | 266 | 0.38882
[16 empty] | 240 | 0.04278 | 240 | 0.0638 | 244 | 0.07665 | 244 | 0.10459 | 251 | 0.12153 | 251 | 0.15926 | 258 | 0.20168 | 258 | 0.25717 | 267 | 0.30691 | 267 | 0.38592
[16 empty] | 241 | 0.04245 | 241 | 0.06337 | 245 | 0.07552 | 245 | 0.10383 | 252 | 0.12065 | 252 | 0.15808 | 259 | 0.20025 | 259 | 0.25524 | 268 | 0.30479 | 268 | 0.38306
[16 empty] | 242 | 0.04213 | 242 | 0.06294 | 246 | 0.07496 | 246 | 0.10308 | 253 | 0.11977 | 253 | 0.15692 | 260 | 0.19883 | 260 | 0.25334 | 269 | 0.30268 | 269 | 0.38023
[16 empty] | 243 | 0.04182 | 243 | 0.06252 | 247 | 0.0744 | 247 | 0.10234 | 254 | 0.11891 | 254 | 0.15576 | 261 | 0.19742 | 261 | 0.25146 | 270 | 0.3006 | 270 | 0.37744
[16 empty] | 244 | 0.0415 | 244 | 0.06211 | 248 | 0.07386 | 248 | 0.10161 | 255 | 0.11805 | 255 | 0.15462 | 262 | 0.19603 | 262 | 0.24961 | 271 | 0.29854 | 271 | 0.37467
[16 empty] | 245 | 0.04089 | 245 | 0.0617 | 249 | 0.07332 | 249 | 0.10088 | 256 | 0.11636 | 256 | 0.1535 | 263 | 0.19466 | 263 | 0.24777 | 272 | 0.29651 | 272 | 0.37194
[16 empty] | 246 | 0.04059 | 246 | 0.06129 | 250 | 0.07278 | 250 | 0.10017 | 257 | 0.11553 | 257 | 0.15239 | 264 | 0.1933 | 264 | 0.24596 | 273 | 0.015625 | 273 | 0.36924
[16 empty] | 247 | 0.04029 | 247 | 0.06089 | 251 | 0.07225 | 251 | 0.09946 | 258 | 0.11471 | 258 | 0.15129 | 265 | 0.19062 | 265 | 0.24416 | 274 | 0.015625 | 274 | 0.36657
[16 empty] | 248 | 0.03999 | 248 | 0.0605 | 252 | 0.07173 | 252 | 0.09877 | 259 | 0.1139 | 259 | 0.1502 | 266 | 0.18931 | 266 | 0.24239 | 275 | 0.015625 | 275 | 0.36393
[16 empty] | 249 | 0.0397 | 249 | 0.06011 | 253 | 0.07121 | 253 | 0.09808 | 260 | 0.1131 | 260 | 0.14913 | 267 | 0.188 | 267 | 0.24064 | 276 | 0.015625 | 276 | 0.36131
[16 empty] | 250 | 0.03941 | 250 | 0.05972 | 254 | 0.0707 | 254 | 0.0974 | 261 | 0.11231 | 261 | 0.14807 | 268 | 0.18671 | 268 | 0.23891 | 277 | 0.015625 | 277 | 0.35873
[16 empty] | 251 | 0.03912 | 251 | 0.05934 | 255 | 0.07019 | 255 | 0.09672 | 262 | 0.11152 | 262 | 0.14702 | 269 | 0.18543 | 269 | 0.23719 | 278 | 0.015625 | 278 | 0.35618
[16 empty] | 252 | 0.03884 | 252 | 0.05896 | 256 | 0.06919 | 256 | 0.09606 | 263 | 0.11074 | 263 | 0.14598 | 270 | 0.18417 | 270 | 0.2355 | 279 | 0.015625 | 279 | 0.35365
[16 empty] | 253 | 0.03856 | 253 | 0.05859 | 257 | 0.0687 | 257 | 0.0954 | 264 | 0.10997 | 264 | 0.14496 | 271 | 0.18292 | 271 | 0.23383 | 280 | 0.015625 | 280 | 0.35116
[16 empty] | 254 | 0.03828 | 254 | 0.05822 | 258 | 0.06822 | 258 | 0.09475 | 265 | 0.10846 | 265 | 0.14395 | 272 | 0.18168 | 272 | 0.23217 | 281 | 0.015625 | 281 | 0.34869
[16 empty] | 255 | 0.03801 | 255 | 0.05786 | 259 | 0.06774 | 259 | 0.09411 | 266 | 0.10771 | 266 | 0.14294 | 273 | 0.015625 | 273 | 0.23053 | 282 | 0.015625 | 282 | 0.34624
[16 empty] | 256 | 0.03747 | 256 | 0.0575 | 260 | 0.06726 | 260 | 0.09348 | 267 | 0.10697 | 267 | 0.14195 | 274 | 0.015625 | 274 | 0.22892 | 283 | 0.015625 | 283 | 0.34383
[16 empty] | 257 | 0.03721 | 257 | 0.05715 | 261 | 0.06679 | 261 | 0.09285 | 268 | 0.10624 | 268 | 0.14098 | 275 | 0.015625 | 275 | 0.22732 | 284 | 0.015625 | 284 | 0.34144
[16 empty] | 258 | 0.03694 | 258 | 0.0568 | 262 | 0.06632 | 262 | 0.09223 | 269 | 0.10552 | 269 | 0.14001 | 276 | 0.015625 | 276 | 0.22573 | 285 | 0.015625 | 285 | 0.33908
[16 empty] | 259 | 0.03668 | 259 | 0.05645 | 263 | 0.06586 | 263 | 0.09162 | 270 | 0.1048 | 270 | 0.13905 | 277 | 0.015625 | 277 | 0.22417 | 286 | 0.015625 | 286 | 0.33674
[16 empty] | 260 | 0.03643 | 260 | 0.05611 | 264 | 0.06541 | 264 | 0.09101 | 271 | 0.1041 | 271 | 0.13811 | 278 | 0.015625 | 278 | 0.22262 | 287 | 0.015625 | 287 | 0.33442
[16 empty] | 261 | 0.03617 | 261 | 0.05577 | 265 | 0.06451 | 265 | 0.09041 | 272 | 0.10339 | 272 | 0.13717 | 279 | 0.015625 | 279 | 0.22109 | 288 | 0.015625 | 288 | 0.33214
[16 empty] | 262 | 0.03592 | 262 | 0.05543 | 266 | 0.06407 | 266 | 0.08982 | 273 | 0.015625 | 273 | 0.13624 | 280 | 0.015625 | 280 | 0.21957 | 289 | 0.015625 | 289 | 0.32987
[16 empty] | 263 | 0.03567 | 263 | 0.0551 | 267 | 0.06363 | 267 | 0.08923 | 274 | 0.015625 | 274 | 0.13533 | 281 | 0.015625 | 281 | 0.21808 | 290 | 0.015625 | 290 | 0.32763
[16 empty] | 264 | 0.03543 | 264 | 0.05478 | 268 | 0.0632 | 268 | 0.08865 | 275 | 0.015625 | 275 | 0.13443 | 282 | 0.015625 | 282 | 0.2166 | 291 | 0.015625 | 291 | 0.32542
[16 empty] | 265 | 0.03494 | 265 | 0.05445 | 269 | 0.06277 | 269 | 0.08808 | 276 | 0.015625 | 276 | 0.13353 | 283 | 0.015625 | 283 | 0.21513 | 292 | 0.015625 | 292 | 0.32323
[16 empty] | 266 | 0.0347 | 266 | 0.05413 | 270 | 0.06235 | 270 | 0.08752 | 277 | 0.015625 | 277 | 0.13265 | 284 | 0.015625 | 284 | 0.21368 | 293 | 0.015625 | 293 | 0.32106
[16 empty] | 267 | 0.03447 | 267 | 0.05382 | 271 | 0.06193 | 271 | 0.08696 | 278 | 0.015625 | 278 | 0.13177 | 285 | 0.015625 | 285 | 0.21225 | 294 | 0.015625 | 294 | 0.31891
[16 empty] | 268 | 0.03423 | 268 | 0.0535 | 272 | 0.06151 | 272 | 0.0864 | 279 | 0.015625 | 279 | 0.13091 | 286 | 0.015625 | 286 | 0.21083 | 295 | 0.015625 | 295 | 0.31679
[16 empty] | 269 | 0.034 | 269 | 0.05319 | 273 | 0.015625 | 273 | 0.08586 | 280 | 0.015625 | 280 | 0.13005 | 287 | 0.015625 | 287 | 0.20942 | 296 | 0.015625 | 296 | 0.31468
[16 empty] | 270 | 0.03377 | 270 | 0.05289 | 274 | 0.015625 | 274 | 0.08532 | 281 | 0.015625 | 281 | 0.1292 | 288 | 0.015625 | 288 | 0.20803 | 297 | 0.015625 | 297 | 0.3126
[16 empty] | 271 | 0.03354 | 271 | 0.05259 | 275 | 0.015625 | 275 | 0.08478 | 282 | 0.015625 | 282 | 0.12836 | 289 | 0.015625 | 289 | 0.20666 | 298 | 0.015625 | 298 | 0.31054
[16 empty] | 272 | 0.03332 | 272 | 0.05229 | 276 | 0.015625 | 276 | 0.08425 | 283 | 0.015625 | 283 | 0.12753 | 290 | 0.015625 | 290 | 0.2053 | 299 | 0.015625 | 299 | 0.30851
[16 empty] | 273 | 0.015625 | 273 | 0.05199 | 277 | 0.015625 | 277 | 0.08373 | 284 | 0.015625 | 284 | 0.12671 | 291 | 0.015625 | 291 | 0.20396 | 300 | 0.015625 | 300 | 0.03334
[16 empty] | 274 | 0.015625 | 274 | 0.0517 | 278 | 0.015625 | 278 | 0.08321 | 285 | 0.015625 | 285 | 0.1259 | 292 | 0.015625 | 292 | 0.20262 | 453 | 0.015625 | 453 | 0.03334
[16 empty] | 275 | 0.015625 | 275 | 0.05141 | 279 | 0.015625 | 279 | 0.0827 | 286 | 0.015625 | 286 | 0.1251 | 293 | 0.015625 | 293 | 0.20131 | 454 | 0.011042 | 454 | 0.03334
[16 empty] | 276 | 0.015625 | 276 | 0.05112 | 280 | 0.015625 | 280 | 0.08219 | 287 | 0.015625 | 287 | 0.12431 | 294 | 0.015625 | 294 | 0.2 | 455 | 0.001 | 455 | 0.03334
[16 empty] | 277 | 0.015625 | 277 | 0.05084 | 281 | 0.015625 | 281 | 0.08169 | 288 | 0.015625 | 288 | 0.12352 | 295 | 0.015625 | 295 | 0.19871 | 500 | 0.001 | 500 | 0.03334
[16 empty] | 278 | 0.015625 | 278 | 0.05056 | 282 | 0.015625 | 282 | 0.08119 | 289 | 0.015625 | 289 | 0.12274 | 296 | 0.015625 | 296 | 0.19743 | 501 | 0.001 | 501 | 0.01667
[16 empty] | 279 | 0.015625 | 279 | 0.05028 | 283 | 0.015625 | 283 | 0.0807 | 290 | 0.015625 | 290 | 0.12197 | 297 | 0.015625 | 297 | 0.19617 | 6300 | 0.001 | 6300 | 0.01667
[16 empty] | 280 | 0.015625 | 280 | 0.05001 | 284 | 0.015625 | 284 | 0.08022 | 291 | 0.015625 | 291 | 0.12121 | 298 | 0.015625 | 298 | 0.19492
[16 empty] | 281 | 0.015625 | 281 | 0.04974 | 285 | 0.015625 | 285 | 0.07974 | 292 | 0.015625 | 292 | 0.12046 | 299 | 0.015625 | 299 | 0.19368
[16 empty] | 282 | 0.015625 | 282 | 0.04947 | 286 | 0.015625 | 286 | 0.07926 | 293 | 0.015625 | 293 | 0.11971 | 300 | 0.015625 | 300 | 0.03334
[16 empty] | 283 | 0.015625 | 283 | 0.04921 | 287 | 0.015625 | 287 | 0.07879 | 294 | 0.015625 | 294 | 0.11897 | 453 | 0.015625 | 453 | 0.03334
[16 empty] | 284 | 0.015625 | 284 | 0.04894 | 288 | 0.015625 | 288 | 0.07832 | 295 | 0.015625 | 295 | 0.11824 | 454 | 0.011042 | 454 | 0.03334
[16 empty] | 285 | 0.015625 | 285 | 0.04868 | 289 | 0.015625 | 289 | 0.07786 | 296 | 0.015625 | 296 | 0.11752 | 455 | 0.001 | 455 | 0.03334
[16 empty] | 286 | 0.015625 | 286 | 0.04843 | 290 | 0.015625 | 290 | 0.07741 | 297 | 0.015625 | 297 | 0.1168 | 500 | 0.001 | 500 | 0.03334
[16 empty] | 287 | 0.015625 | 287 | 0.04817 | 291 | 0.015625 | 291 | 0.07696 | 298 | 0.015625 | 298 | 0.1161 | 501 | 0.001 | 501 | 0.01667
[16 empty] | 288 | 0.015625 | 288 | 0.04792 | 292 | 0.015625 | 292 | 0.07651 | 299 | 0.015625 | 299 | 0.11539 | 6300 | 0.001 | 6300 | 0.01667
[16 empty] | 289 | 0.015625 | 289 | 0.04767 | 293 | 0.015625 | 293 | 0.07607 | 300 | 0.015625 | 300 | 0.03334
[16 empty] | 290 | 0.015625 | 290 | 0.04743 | 294 | 0.015625 | 294 | 0.07563 | 453 | 0.015625 | 453 | 0.03334
[16 empty] | 291 | 0.015625 | 291 | 0.04718 | 295 | 0.015625 | 295 | 0.0752 | 454 | 0.011042 | 454 | 0.03334
[16 empty] | 292 | 0.015625 | 292 | 0.04694 | 296 | 0.015625 | 296 | 0.07477 | 455 | 0.001 | 455 | 0.03334
[16 empty] | 293 | 0.015625 | 293 | 0.0467 | 297 | 0.015625 | 297 | 0.07435 | 500 | 0.001 | 500 | 0.03334
[16 empty] | 294 | 0.015625 | 294 | 0.04647 | 298 | 0.015625 | 298 | 0.07393 | 501 | 0.001 | 501 | 0.01667
[16 empty] | 295 | 0.015625 | 295 | 0.04623 | 299 | 0.015625 | 299 | 0.07351 | 6300 | 0.001 | 6300 | 0.01667
[16 empty] | 296 | 0.015625 | 296 | 0.046 | 300 | 0.015625 | 300 | 0.03334
[16 empty] | 297 | 0.015625 | 297 | 0.04577 | 453 | 0.015625 | 453 | 0.03334
[16 empty] | 298 | 0.015625 | 298 | 0.04554 | 454 | 0.011042 | 454 | 0.03334
[16 empty] | 299 | 0.015625 | 299 | 0.04532 | 455 | 0.001 | 455 | 0.03334
[16 empty] | 300 | 0.015625 | 300 | 0.03334 | 500 | 0.001 | 500 | 0.03334
[16 empty] | 453 | 0.015625 | 453 | 0.03334 | 501 | 0.001 | 501 | 0.01667
[16 empty] | 454 | 0.011042 | 454 | 0.03334 | 6300 | 0.001 | 6300 | 0.01667
[16 empty] | 455 | 0.001 | 455 | 0.03334
[16 empty] | 500 | 0.001 | 500 | 0.03334
[16 empty] | 501 | 0.001 | 501 | 0.01667
[16 empty] | 6300 | 0.001 | 6300 | 0.01667

## S&C "TXP" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "TXP" Speed | [11 empty] | S&C "TXP" Speed | [11 empty] | S&C "TXP" Speed | [11 empty] | S&C "TXP" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated March 13, 2023
Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 1 of S&C Information Bulletin 466-211 for tolerance information.
2TXP |  |  |  | 3TXP |  |  |  | 5TXP |  |  |  | 6TXP |  |  |  | 7TXP |  |  |  | 8TXP |  |  |  | 10TXP |  |  |  | 12TXP |  |  |  | 15TXP |  |  |  | 20TXP
Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s
4 | 260.0334 | 4 | 671.4795 | 6 | 339.7704 | 6 | 671.4795 | 10 | 440.6662 | 10 | 671.4795 | 12 | 471.4226 | 12 | 671.4795 | 14 | 495.0132 | 14 | 671.4795 | 16 | 399.0073 | 16 | 671.4795 | 20 | 440.6662 | 20 | 671.4795 | 24 | 471.4226 | 24 | 671.4795 | 30 | 440.6662 | 30 | 671.4795 | 40 | 440.6662 | 40 | 671.4795
5 | 137.3123 | 5 | 260.0454 | 7 | 207.4259 | 7 | 339.7824 | 11 | 300 | 11 | 440.6782 | 13 | 339.7704 | 13 | 471.4346 | 15 | 372.1836 | 15 | 495.0252 | 17 | 314.2081 | 17 | 513.6732 | 21 | 362.0761 | 21 | 541.2509 | 25 | 339.7704 | 25 | 560.6482 | 31 | 386.2044 | 31 | 580.905 | 41 | 399.0073 | 41 | 602.0667
6 | 80.0275 | 6 | 137.3243 | 8 | 137.3123 | 8 | 207.4379 | 12 | 226.6588 | 12 | 300.012 | 14 | 260.0334 | 14 | 339.7824 | 16 | 235.6025 | 16 | 372.1956 | 18 | 260.0334 | 18 | 399.0193 | 22 | 300 | 22 | 440.6782 | 26 | 292.8161 | 26 | 471.4346 | 32 | 339.7704 | 32 | 504.8655 | 42 | 362.0761 | 42 | 541.2509
7 | 52.9024 | 7 | 80.0395 | 9 | 94.9405 | 9 | 137.3243 | 13 | 174.8441 | 13 | 226.6708 | 15 | 207.4259 | 15 | 260.0454 | 17 | 194.958 | 17 | 287.8317 | 19 | 219.1881 | 19 | 314.2201 | 23 | 260.0334 | 23 | 362.0881 | 27 | 260.0334 | 27 | 399.0193 | 33 | 300 | 33 | 440.6782 | 43 | 329.2502 | 43 | 487.799
8 | 39.6209 | 8 | 52.9144 | 10 | 67.9955 | 10 | 94.9525 | 14 | 137.3123 | 14 | 174.8561 | 16 | 137.3123 | 16 | 207.4379 | 18 | 162.9002 | 18 | 235.6145 | 20 | 186.2335 | 20 | 260.0454 | 24 | 226.6588 | 24 | 300.012 | 28 | 231.8218 | 28 | 339.7824 | 34 | 272.55 | 34 | 386.2164 | 44 | 300 | 44 | 440.6782
9 | 30.5925 | 9 | 39.6329 | 11 | 52.9024 | 11 | 68.0075 | 15 | 109.5326 | 15 | 137.3243 | 17 | 113.6242 | 17 | 167.7572 | 19 | 137.3123 | 19 | 194.97 | 21 | 159.384 | 21 | 219.2001 | 25 | 174.8441 | 25 | 260.0454 | 29 | 207.4259 | 29 | 292.8281 | 35 | 248.2461 | 35 | 339.7824 | 45 | 260.0334 | 45 | 399.0193
10 | 25.4563 | 10 | 30.6045 | 12 | 43.4664 | 12 | 52.9144 | 16 | 72.5087 | 16 | 109.5446 | 18 | 94.9405 | 18 | 137.3243 | 20 | 116.6676 | 20 | 162.9122 | 22 | 137.3123 | 22 | 186.2455 | 26 | 154.6235 | 26 | 226.6708 | 30 | 186.2335 | 30 | 260.0454 | 36 | 207.4259 | 36 | 300.012 | 46 | 242.6098 | 46 | 362.0881
11 | 21.6141 | 11 | 25.4683 | 13 | 36.2375 | 13 | 43.4784 | 17 | 60 | 17 | 88.591 | 19 | 80.0275 | 19 | 113.6362 | 21 | 99.8475 | 21 | 137.3243 | 23 | 119.0193 | 23 | 159.396 | 27 | 137.3123 | 27 | 198.6068 | 31 | 167.7452 | 31 | 231.8338 | 37 | 190.2411 | 37 | 272.562 | 47 | 226.6588 | 47 | 329.2622
12 | 18.594 | 12 | 21.6261 | 14 | 30.5925 | 14 | 36.2495 | 18 | 52.9024 | 18 | 72.5207 | 20 | 67.9955 | 20 | 94.9525 | 22 | 86.0205 | 22 | 116.6796 | 24 | 103.7435 | 24 | 137.3243 | 28 | 122.415 | 28 | 174.8561 | 32 | 151.551 | 32 | 207.4379 | 38 | 174.8441 | 38 | 248.2581 | 48 | 212.031 | 48 | 300.012
13 | 16.1753 | 13 | 18.606 | 15 | 26.9727 | 15 | 30.6045 | 19 | 46.9318 | 19 | 60.012 | 21 | 58.7275 | 21 | 80.0395 | 23 | 74.5607 | 23 | 99.8595 | 25 | 80.0275 | 25 | 119.0313 | 29 | 109.5326 | 29 | 154.6355 | 33 | 137.3123 | 33 | 186.2455 | 39 | 161.0126 | 39 | 226.6708 | 49 | 198.5948 | 49 | 279.111
14 | 14.2073 | 14 | 16.1873 | 16 | 21.6141 | 16 | 26.9847 | 20 | 41.8677 | 20 | 52.9144 | 22 | 52.9024 | 22 | 68.0075 | 24 | 64.991 | 24 | 86.0325 | 26 | 70.7724 | 26 | 103.7555 | 30 | 98.3418 | 30 | 137.3243 | 34 | 124.7482 | 34 | 167.7572 | 40 | 148.5565 | 40 | 207.4379 | 50 | 186.2335 | 50 | 260.0454
15 | 12.5837 | 15 | 14.2193 | 17 | 19.5247 | 17 | 24.0787 | 21 | 37.5401 | 21 | 46.9438 | 23 | 47.8587 | 23 | 58.7395 | 25 | 52.9024 | 25 | 74.5727 | 27 | 62.8489 | 27 | 90.9104 | 31 | 88.579 | 31 | 122.427 | 35 | 113.6242 | 35 | 151.563 | 41 | 137.3123 | 41 | 190.2531 | 51 | 174.8441 | 51 | 242.6218
16 | 10.0837 | 16 | 12.5957 | 18 | 17.7295 | 18 | 21.6261 | 22 | 33.8165 | 22 | 41.8797 | 24 | 43.4664 | 24 | 52.9144 | 26 | 48.5366 | 26 | 65.003 | 28 | 57.1897 | 28 | 80.0395 | 32 | 80.0275 | 32 | 109.5446 | 36 | 94.9405 | 36 | 137.3243 | 42 | 127.1389 | 42 | 174.8561 | 52 | 164.3346 | 52 | 226.6708
17 | 9.043 | 17 | 11.2399 | 19 | 16.1753 | 19 | 19.5367 | 23 | 30.5925 | 23 | 37.5521 | 25 | 36.2375 | 25 | 47.8707 | 27 | 44.6614 | 27 | 57.8537 | 29 | 52.9024 | 29 | 70.7844 | 33 | 72.5087 | 33 | 98.3538 | 37 | 87.0748 | 37 | 124.7602 | 43 | 117.9144 | 43 | 161.0246 | 53 | 154.6235 | 53 | 212.043
18 | 8.1501 | 18 | 10.0957 | 20 | 14.8205 | 20 | 17.7415 | 24 | 28.2878 | 24 | 33.8285 | 26 | 33.247 | 26 | 43.4784 | 28 | 41.2078 | 28 | 52.9144 | 30 | 49.054 | 30 | 62.8609 | 34 | 65.8741 | 34 | 88.591 | 38 | 80.0275 | 38 | 113.6362 | 44 | 109.5326 | 44 | 148.5685 | 54 | 145.6378 | 54 | 198.6068
19 | 7.3827 | 19 | 9.055 | 21 | 13.6321 | 21 | 16.1873 | 25 | 24.6082 | 25 | 30.6045 | 27 | 30.5925 | 27 | 39.6329 | 29 | 38.1186 | 29 | 48.5486 | 31 | 45.5882 | 31 | 57.2017 | 35 | 60 | 35 | 80.0395 | 39 | 73.6967 | 39 | 103.7555 | 45 | 94.9405 | 45 | 137.3243 | 55 | 129.5889 | 55 | 186.2455
20 | 6.7184 | 20 | 8.1621 | 22 | 12.5837 | 22 | 14.8325 | 26 | 23.0369 | 26 | 28.2998 | 28 | 28.632 | 28 | 36.2495 | 30 | 35.3457 | 30 | 44.6734 | 32 | 42.4573 | 32 | 52.9144 | 36 | 52.9024 | 36 | 72.5207 | 40 | 67.9955 | 40 | 94.9525 | 46 | 88.579 | 46 | 127.1509 | 56 | 122.415 | 56 | 174.8561
21 | 6.1396 | 21 | 7.3947 | 23 | 11.6539 | 23 | 13.6441 | 27 | 21.6141 | 27 | 26.3619 | 29 | 26.9727 | 29 | 33.259 | 31 | 32.8484 | 31 | 41.2198 | 33 | 39.6209 | 33 | 49.066 | 37 | 49.7914 | 37 | 65.8861 | 41 | 62.8489 | 41 | 87.0868 | 47 | 82.7551 | 47 | 117.9264 | 57 | 115.7437 | 57 | 164.3466
22 | 5.6322 | 22 | 6.7304 | 24 | 10.8253 | 24 | 12.5957 | 28 | 20.3217 | 28 | 24.6202 | 30 | 25.4563 | 30 | 30.6045 | 32 | 30.5925 | 32 | 38.1306 | 34 | 37.044 | 34 | 45.6002 | 38 | 46.9318 | 38 | 60.012 | 42 | 58.7275 | 42 | 80.0395 | 48 | 77.4144 | 48 | 109.5446 | 58 | 109.5326 | 58 | 154.6355
23 | 5.1849 | 23 | 6.1516 | 25 | 9.3733 | 25 | 11.6659 | 29 | 19.1441 | 29 | 23.0489 | 31 | 24.0667 | 31 | 28.644 | 33 | 28.8817 | 33 | 35.3577 | 35 | 34.6969 | 35 | 42.4693 | 39 | 44.2981 | 39 | 56.3061 | 43 | 55.7079 | 43 | 73.7087 | 49 | 72.5087 | 49 | 101.9135 | 59 | 103.7435 | 59 | 145.6498
24 | 4.7887 | 24 | 5.6442 | 26 | 8.7298 | 26 | 10.8373 | 30 | 18.0678 | 30 | 21.6261 | 32 | 22.79 | 32 | 26.9847 | 34 | 27.4314 | 34 | 32.8604 | 36 | 30.5925 | 36 | 39.6329 | 40 | 41.8677 | 40 | 52.9144 | 44 | 52.9024 | 44 | 68.0075 | 50 | 67.9955 | 50 | 94.9525 | 60 | 98.3418 | 60 | 137.3243
25 | 4.1209 | 25 | 5.1969 | 27 | 8.1501 | 27 | 10.0957 | 31 | 17.0815 | 31 | 20.3337 | 33 | 21.6141 | 33 | 25.4683 | 35 | 26.0897 | 35 | 30.6045 | 37 | 29.0712 | 37 | 37.056 | 41 | 39.6209 | 41 | 49.8034 | 45 | 47.8587 | 45 | 62.8609 | 51 | 63.8371 | 51 | 88.591 | 61 | 93.2964 | 61 | 129.6009
26 | 3.838 | 26 | 4.8007 | 28 | 7.626 | 28 | 9.3853 | 32 | 16.1753 | 32 | 19.1561 | 34 | 20.5288 | 34 | 24.0787 | 36 | 23.6909 | 36 | 28.8937 | 38 | 27.7833 | 38 | 34.7089 | 42 | 37.5401 | 42 | 46.9438 | 46 | 45.5882 | 46 | 58.7395 | 52 | 60 | 52 | 82.7671 | 62 | 88.579 | 62 | 122.427
27 | 3.5831 | 27 | 4.4481 | 29 | 7.1508 | 29 | 8.7418 | 33 | 15.3408 | 33 | 18.0798 | 35 | 19.5247 | 35 | 22.802 | 37 | 22.6161 | 37 | 27.4434 | 39 | 26.5809 | 39 | 32.5659 | 43 | 35.6099 | 43 | 44.3101 | 47 | 43.4664 | 47 | 55.7199 | 53 | 57.4927 | 53 | 77.4264 | 63 | 84.1638 | 63 | 115.7557
28 | 3.3527 | 28 | 4.1329 | 30 | 6.7184 | 30 | 8.1621 | 34 | 14.5705 | 34 | 17.0935 | 36 | 17.7295 | 36 | 21.6261 | 38 | 21.6141 | 38 | 26.1017 | 40 | 25.4563 | 40 | 30.6045 | 44 | 33.8165 | 44 | 41.8797 | 48 | 41.481 | 48 | 52.9144 | 54 | 55.1303 | 54 | 72.5207 | 64 | 80.0275 | 64 | 109.5446
29 | 3.1437 | 29 | 3.85 | 31 | 6.3239 | 31 | 7.638 | 35 | 13.8578 | 35 | 16.1873 | 37 | 16.9251 | 37 | 20.5408 | 39 | 20.6787 | 39 | 24.858 | 41 | 24.403 | 41 | 29.0832 | 45 | 30.5925 | 45 | 39.6329 | 49 | 39.6209 | 49 | 50.3037 | 55 | 50.7991 | 55 | 68.0075 | 65 | 72.5087 | 65 | 103.7555
30 | 2.9537 | 30 | 3.5951 | 32 | 5.9631 | 32 | 7.1628 | 36 | 12.5837 | 36 | 15.3528 | 38 | 16.1753 | 38 | 19.5367 | 40 | 19.8038 | 40 | 23.7029 | 42 | 23.415 | 42 | 27.7953 | 46 | 29.3398 | 46 | 37.5521 | 50 | 37.8761 | 50 | 47.8707 | 56 | 48.8116 | 56 | 63.8491 | 66 | 69.0891 | 66 | 98.3538
31 | 2.7803 | 31 | 3.3647 | 33 | 5.6322 | 33 | 6.7304 | 37 | 12.0128 | 37 | 14.5825 | 39 | 15.4753 | 39 | 18.606 | 41 | 18.9844 | 41 | 22.6281 | 43 | 22.487 | 43 | 26.5928 | 47 | 28.2878 | 47 | 35.6219 | 51 | 36.2375 | 51 | 45.6002 | 57 | 46.9318 | 57 | 60.012 | 67 | 65.8741 | 67 | 93.3084
32 | 2.6216 | 32 | 3.1557 | 34 | 5.3279 | 34 | 6.336 | 38 | 11.4806 | 38 | 13.8698 | 40 | 14.8205 | 40 | 17.7415 | 42 | 18.2158 | 42 | 21.6261 | 44 | 21.6141 | 44 | 25.4683 | 48 | 27.2925 | 48 | 33.8285 | 52 | 34.6969 | 52 | 43.4784 | 58 | 45.1523 | 58 | 57.5047 | 68 | 62.8489 | 68 | 88.591
33 | 2.4761 | 33 | 2.9657 | 35 | 5.0476 | 35 | 5.9751 | 39 | 10.9837 | 39 | 13.2092 | 41 | 14.2073 | 41 | 16.9371 | 43 | 17.4938 | 43 | 20.6907 | 45 | 20.0171 | 45 | 24.415 | 49 | 26.3499 | 49 | 32.1597 | 53 | 33.247 | 53 | 41.493 | 59 | 43.4664 | 59 | 55.1423 | 69 | 60 | 69 | 84.1758
34 | 2.3424 | 34 | 2.7923 | 36 | 4.5492 | 36 | 5.6442 | 40 | 10.519 | 40 | 12.5957 | 42 | 13.6321 | 42 | 16.1873 | 44 | 16.8148 | 44 | 19.8158 | 46 | 19.2855 | 46 | 23.427 | 50 | 25.4563 | 50 | 30.6045 | 54 | 31.8809 | 54 | 39.6329 | 60 | 41.8677 | 60 | 52.9144 | 70 | 58.1055 | 70 | 80.0395
35 | 2.2191 | 35 | 2.6336 | 37 | 4.3271 | 37 | 5.3399 | 41 | 10.0837 | 41 | 12.0247 | 43 | 13.0918 | 43 | 15.4872 | 45 | 15.5724 | 45 | 18.9964 | 47 | 18.594 | 47 | 22.499 | 51 | 24.6082 | 51 | 29.3518 | 55 | 29.5209 | 55 | 37.8881 | 61 | 40.3505 | 61 | 50.8111 | 71 | 56.2941 | 71 | 76.1609
36 | 2 | 36 | 2.4881 | 38 | 4.1209 | 38 | 5.0596 | 42 | 9.6507 | 42 | 11.4926 | 44 | 12.5837 | 44 | 14.8325 | 46 | 15.0032 | 46 | 18.2278 | 48 | 17.9398 | 48 | 21.6261 | 52 | 23.8027 | 52 | 28.2998 | 56 | 28.632 | 56 | 36.2495 | 62 | 38.9096 | 62 | 48.8236 | 72 | 54.5611 | 72 | 72.5207
37 | 1.9036 | 37 | 2.3544 | 39 | 3.9289 | 39 | 4.8007 | 43 | 9.239 | 43 | 10.9957 | 45 | 11.6539 | 45 | 14.2193 | 47 | 14.4653 | 47 | 17.5058 | 49 | 17.3202 | 49 | 20.8042 | 53 | 23.0369 | 53 | 27.3045 | 57 | 27.7833 | 57 | 34.7089 | 63 | 37.5401 | 63 | 46.9438 | 73 | 52.9024 | 73 | 69.1011
38 | 1.8141 | 38 | 2.2311 | 40 | 3.7501 | 40 | 4.5612 | 44 | 8.8531 | 44 | 10.531 | 46 | 11.2279 | 46 | 13.6441 | 48 | 13.9563 | 48 | 16.8268 | 50 | 16.7328 | 50 | 20.0291 | 54 | 22.3082 | 54 | 26.3619 | 58 | 26.9727 | 58 | 33.259 | 64 | 36.2375 | 64 | 45.1643 | 74 | 51.3137 | 74 | 65.8861
39 | 1.7307 | 39 | 2.1173 | 41 | 3.5831 | 41 | 4.3391 | 45 | 8.1501 | 45 | 10.0957 | 47 | 10.8253 | 47 | 13.1038 | 49 | 13.4743 | 49 | 16.1873 | 51 | 16.1753 | 51 | 19.2975 | 55 | 20.9527 | 55 | 25.4683 | 59 | 26.1977 | 59 | 31.8929 | 65 | 33.8165 | 65 | 43.4784 | 75 | 49.7914 | 75 | 62.8609
40 | 1.6529 | 40 | 2.012 | 42 | 3.427 | 42 | 4.1329 | 46 | 7.8294 | 46 | 9.6627 | 48 | 10.4445 | 48 | 12.5957 | 50 | 13.0173 | 50 | 15.5844 | 52 | 15.6459 | 52 | 18.606 | 56 | 20.3217 | 56 | 24.6202 | 60 | 25.4563 | 60 | 30.6045 | 66 | 32.6908 | 66 | 41.8797 | 76 | 46.9318 | 76 | 60.012
41 | 1.5802 | 41 | 1.9156 | 43 | 3.2808 | 43 | 3.9409 | 47 | 7.5273 | 47 | 9.251 | 49 | 10.0837 | 49 | 12.1171 | 51 | 12.5837 | 51 | 15.0152 | 53 | 15.1425 | 53 | 17.9518 | 57 | 19.7194 | 57 | 23.8147 | 61 | 24.7465 | 61 | 29.5329 | 67 | 31.6172 | 67 | 40.3625 | 77 | 45.5882 | 77 | 58.1175
42 | 1.5123 | 42 | 1.8261 | 44 | 3.1437 | 44 | 3.7621 | 48 | 7.2422 | 48 | 8.8651 | 50 | 9.7219 | 50 | 11.6659 | 52 | 12.1717 | 52 | 14.4773 | 54 | 14.6635 | 54 | 17.3322 | 58 | 19.1441 | 58 | 23.0489 | 62 | 24.0667 | 62 | 28.644 | 68 | 30.5925 | 68 | 38.9216 | 78 | 44.2981 | 78 | 56.3061
43 | 1.4486 | 43 | 1.7427 | 45 | 2.8941 | 45 | 3.5951 | 49 | 6.973 | 49 | 8.5027 | 51 | 9.3733 | 51 | 11.2399 | 53 | 11.7801 | 53 | 13.9683 | 55 | 13.7725 | 55 | 16.7448 | 59 | 18.594 | 59 | 22.3202 | 63 | 23.415 | 63 | 27.7953 | 69 | 29.7038 | 69 | 37.5521 | 79 | 43.0588 | 79 | 54.5731
44 | 1.3889 | 44 | 1.6649 | 46 | 2.7803 | 46 | 3.439 | 50 | 6.7184 | 50 | 8.1621 | 52 | 9.043 | 52 | 10.8373 | 54 | 11.4075 | 54 | 13.4863 | 56 | 13.3578 | 56 | 16.1873 | 60 | 18.0678 | 60 | 21.6261 | 64 | 22.79 | 64 | 26.9847 | 70 | 28.9826 | 70 | 36.2495 | 80 | 41.8677 | 80 | 52.9144
45 | 1.28 | 45 | 1.5922 | 47 | 2.673 | 47 | 3.2928 | 51 | 6.4775 | 51 | 7.8414 | 53 | 8.7298 | 53 | 10.4565 | 55 | 10.7144 | 55 | 13.0293 | 57 | 12.9619 | 57 | 15.6579 | 61 | 17.564 | 61 | 20.9647 | 65 | 21.6141 | 65 | 26.2097 | 71 | 28.2878 | 71 | 35.0096 | 81 | 40.7225 | 81 | 51.3257
46 | 1.2303 | 46 | 1.5243 | 48 | 2.5717 | 48 | 3.1557 | 52 | 6.2492 | 52 | 7.5393 | 54 | 8.4325 | 54 | 10.0957 | 56 | 10.3917 | 56 | 12.5957 | 58 | 12.5837 | 58 | 15.1545 | 62 | 17.0815 | 62 | 20.3337 | 66 | 21.0608 | 66 | 25.4683 | 72 | 27.6182 | 72 | 33.8285 | 82 | 39.6209 | 82 | 49.8034
47 | 1.1834 | 47 | 1.4606 | 49 | 2.4761 | 49 | 3.0271 | 53 | 6.0328 | 53 | 7.2542 | 55 | 7.8816 | 55 | 9.7339 | 57 | 10.0837 | 57 | 12.1837 | 59 | 12.2221 | 59 | 14.6755 | 63 | 16.619 | 63 | 19.7314 | 67 | 20.5288 | 67 | 24.7585 | 73 | 26.9727 | 73 | 32.7028 | 83 | 38.5607 | 83 | 48.3438
48 | 1.1392 | 48 | 1.4009 | 50 | 2.3857 | 50 | 2.9061 | 54 | 5.8273 | 54 | 6.985 | 56 | 7.626 | 56 | 9.3853 | 58 | 9.7733 | 58 | 11.7921 | 60 | 11.8762 | 60 | 14.2193 | 64 | 16.1753 | 64 | 19.1561 | 68 | 20.0171 | 68 | 24.0787 | 74 | 26.3499 | 74 | 31.6292 | 84 | 37.5401 | 84 | 46.9438
49 | 1.0974 | 49 | 1.3448 | 51 | 2.3002 | 51 | 2.7923 | 55 | 5.4466 | 55 | 6.7304 | 57 | 7.3827 | 57 | 9.055 | 59 | 9.471 | 59 | 11.4195 | 61 | 11.5451 | 61 | 13.7845 | 65 | 15.3408 | 65 | 18.606 | 69 | 19.5247 | 69 | 23.427 | 75 | 25.7489 | 75 | 30.6045 | 85 | 35.6099 | 85 | 45.6002
50 | 1.0578 | 50 | 1.292 | 52 | 2.2191 | 52 | 2.685 | 56 | 5.27 | 56 | 6.4895 | 58 | 7.1508 | 58 | 8.7418 | 60 | 9.1824 | 60 | 11.0646 | 62 | 11.2279 | 62 | 13.3698 | 66 | 14.948 | 66 | 18.0798 | 70 | 19.0507 | 70 | 22.802 | 76 | 24.6082 | 76 | 29.7158 | 86 | 34.6969 | 86 | 44.3101
51 | 1.0204 | 51 | 1.2423 | 53 | 2.1423 | 53 | 2.5837 | 57 | 5.1019 | 57 | 6.2612 | 59 | 6.9295 | 59 | 8.4445 | 61 | 8.9067 | 61 | 10.7264 | 63 | 10.9239 | 63 | 12.9739 | 67 | 14.5705 | 67 | 17.576 | 71 | 18.594 | 71 | 22.2021 | 77 | 24.0667 | 77 | 28.9946 | 87 | 33.8165 | 87 | 43.0708
52 | 0.98492 | 52 | 1.1954 | 54 | 2.0693 | 54 | 2.4881 | 58 | 4.9416 | 58 | 6.0448 | 60 | 6.7184 | 60 | 8.1621 | 62 | 8.6433 | 62 | 10.4037 | 64 | 10.6323 | 64 | 12.5957 | 68 | 14.2073 | 68 | 17.0935 | 72 | 18.1539 | 72 | 21.6261 | 78 | 23.5431 | 78 | 28.2998 | 88 | 32.9673 | 88 | 41.8797
53 | 0.95125 | 53 | 1.1512 | 55 | 1.935 | 55 | 2.3977 | 59 | 4.7887 | 59 | 5.8393 | 61 | 6.5167 | 61 | 7.8936 | 63 | 8.3913 | 63 | 10.0957 | 65 | 10.0837 | 65 | 12.2341 | 69 | 13.8578 | 69 | 16.631 | 73 | 17.7295 | 73 | 21.0728 | 79 | 23.0369 | 79 | 27.6303 | 89 | 32.1477 | 89 | 40.7345
54 | 0.91928 | 54 | 1.1094 | 56 | 1.8731 | 56 | 2.3122 | 60 | 4.6428 | 60 | 5.6442 | 62 | 6.3239 | 62 | 7.638 | 64 | 8.1501 | 64 | 9.7853 | 66 | 9.8121 | 66 | 11.8882 | 70 | 13.5213 | 70 | 16.1873 | 74 | 17.3202 | 74 | 20.5408 | 80 | 22.5471 | 80 | 26.9847 | 90 | 31.3565 | 90 | 39.6329
55 | 0.85998 | 55 | 1.0698 | 57 | 1.8141 | 57 | 2.2311 | 61 | 4.5034 | 61 | 5.4586 | 63 | 6.1396 | 63 | 7.3947 | 65 | 7.6978 | 65 | 9.483 | 67 | 9.5452 | 67 | 11.5571 | 71 | 13.1972 | 71 | 15.7616 | 75 | 16.9251 | 75 | 20.0291 | 81 | 22.0731 | 81 | 26.3619 | 91 | 30.5925 | 91 | 38.5727
56 | 0.83247 | 56 | 1.0324 | 58 | 1.7578 | 58 | 2.1543 | 62 | 4.3702 | 62 | 5.282 | 64 | 5.9631 | 64 | 7.1628 | 66 | 7.4855 | 66 | 9.1944 | 68 | 9.289 | 68 | 11.2399 | 72 | 12.8849 | 72 | 15.3528 | 76 | 16.1753 | 76 | 19.5367 | 82 | 21.6141 | 82 | 25.7609 | 92 | 29.8884 | 92 | 37.5521
57 | 0.80625 | 57 | 0.99692 | 59 | 1.7041 | 59 | 2.0813 | 63 | 4.2428 | 63 | 5.1139 | 65 | 5.6322 | 65 | 6.9416 | 67 | 7.2819 | 67 | 8.9187 | 69 | 9.043 | 69 | 10.9359 | 73 | 12.5837 | 73 | 14.96 | 77 | 15.8194 | 77 | 19.0627 | 83 | 21.1697 | 83 | 25.1807 | 93 | 29.3398 | 93 | 36.5691
58 | 0.78125 | 58 | 0.96325 | 60 | 1.6529 | 60 | 2.012 | 64 | 4.1209 | 64 | 4.9536 | 66 | 5.4769 | 66 | 6.7304 | 68 | 7.0865 | 68 | 8.6553 | 70 | 8.8065 | 70 | 10.6443 | 74 | 12.2931 | 74 | 14.5825 | 78 | 15.4753 | 78 | 18.606 | 84 | 20.7391 | 84 | 24.6202 | 94 | 28.8064 | 94 | 35.6219
59 | 0.7574 | 59 | 0.93128 | 61 | 1.6039 | 61 | 1.947 | 65 | 3.8922 | 65 | 4.8007 | 67 | 5.3279 | 67 | 6.5287 | 69 | 6.8988 | 69 | 8.4033 | 71 | 8.5792 | 71 | 10.3644 | 75 | 12.0128 | 75 | 14.2193 | 79 | 15.1425 | 79 | 18.1659 | 85 | 19.9171 | 85 | 24.0787 | 95 | 27.7833 | 95 | 34.7089
60 | 0.73462 | 60 | 0.90089 | 62 | 1.5571 | 62 | 1.885 | 66 | 3.7849 | 66 | 4.6548 | 68 | 5.1849 | 68 | 6.336 | 70 | 6.7184 | 70 | 8.1621 | 72 | 8.3605 | 72 | 10.0957 | 76 | 11.4806 | 76 | 13.8698 | 80 | 14.8205 | 80 | 17.7415 | 86 | 19.5247 | 86 | 23.5551 | 96 | 27.2925 | 96 | 33.8285
61 | 0.71285 | 61 | 0.87198 | 63 | 1.5123 | 63 | 1.8261 | 67 | 3.6819 | 67 | 4.5154 | 69 | 5.0476 | 69 | 6.1516 | 71 | 6.545 | 71 | 7.9311 | 73 | 8.1501 | 73 | 9.8241 | 77 | 11.2279 | 77 | 13.5334 | 81 | 14.509 | 81 | 17.3322 | 87 | 19.1441 | 87 | 23.0489 | 97 | 26.8149 | 97 | 32.9793
62 | 0.69204 | 62 | 0.84447 | 64 | 1.4694 | 64 | 1.7698 | 68 | 3.5831 | 68 | 4.3822 | 70 | 4.9156 | 70 | 5.9751 | 72 | 6.3781 | 72 | 7.7098 | 74 | 7.9474 | 74 | 9.5572 | 78 | 10.9837 | 78 | 13.2092 | 82 | 14.2073 | 82 | 16.9371 | 88 | 18.7746 | 88 | 22.5591 | 98 | 26.3499 | 98 | 32.1597
63 | 0.67213 | 63 | 0.81825 | 65 | 1.3889 | 65 | 1.7161 | 69 | 3.4882 | 69 | 4.2548 | 71 | 4.7887 | 71 | 5.8061 | 73 | 6.2176 | 73 | 7.4975 | 75 | 7.7522 | 75 | 9.301 | 79 | 10.7475 | 79 | 12.8969 | 83 | 13.9152 | 83 | 16.5557 | 89 | 18.416 | 89 | 22.0851 | 99 | 25.8972 | 99 | 31.3685
64 | 0.65306 | 64 | 0.79325 | 66 | 1.3511 | 66 | 1.6649 | 70 | 3.397 | 70 | 4.1329 | 72 | 4.6667 | 72 | 5.6442 | 74 | 6.063 | 74 | 7.2939 | 76 | 7.3827 | 76 | 9.055 | 80 | 10.519 | 80 | 12.5957 | 84 | 13.6321 | 84 | 16.1873 | 90 | 18.0678 | 90 | 21.6261 | 100 | 25.4563 | 100 | 30.6045
65 | 0.61728 | 65 | 0.7694 | 67 | 1.3148 | 67 | 1.6159 | 71 | 3.3093 | 71 | 4.0161 | 73 | 4.5492 | 73 | 5.4889 | 75 | 5.9141 | 75 | 7.0985 | 77 | 7.2077 | 77 | 8.8185 | 81 | 10.2978 | 81 | 12.3051 | 85 | 13.0918 | 85 | 15.8314 | 91 | 17.7295 | 91 | 21.1817 | 101 | 25.0267 | 101 | 29.9004
66 | 0.60049 | 66 | 0.74662 | 68 | 1.28 | 68 | 1.5691 | 72 | 3.2249 | 72 | 3.9042 | 74 | 4.4361 | 74 | 5.3399 | 76 | 5.6322 | 76 | 6.9108 | 78 | 7.0389 | 78 | 8.5912 | 82 | 10.0837 | 82 | 12.0247 | 86 | 12.8339 | 86 | 15.4872 | 92 | 17.4009 | 92 | 20.7511 | 102 | 24.6082 | 102 | 29.3518
67 | 0.58437 | 67 | 0.72485 | 69 | 1.2465 | 69 | 1.5243 | 73 | 3.1437 | 73 | 3.7969 | 75 | 4.3271 | 75 | 5.1969 | 77 | 5.4987 | 77 | 6.7304 | 79 | 6.8758 | 79 | 8.3725 | 83 | 9.8668 | 83 | 11.754 | 87 | 12.5837 | 87 | 15.1545 | 93 | 17.0815 | 93 | 20.3337 | 103 | 24.2003 | 103 | 28.8184
68 | 0.56889 | 68 | 0.70404 | 70 | 1.2144 | 70 | 1.4814 | 74 | 3.0656 | 74 | 3.6939 | 76 | 4.1209 | 76 | 5.0596 | 78 | 5.3699 | 78 | 6.557 | 80 | 6.7184 | 80 | 8.1621 | 84 | 9.6507 | 84 | 11.4926 | 88 | 12.3408 | 88 | 14.8325 | 94 | 16.771 | 94 | 19.9291 | 104 | 23.8027 | 104 | 28.2998
69 | 0.55402 | 69 | 0.68413 | 71 | 1.1834 | 71 | 1.4403 | 75 | 2.9903 | 75 | 3.5951 | 77 | 4.0232 | 77 | 4.9276 | 79 | 5.2455 | 79 | 6.3902 | 81 | 6.5663 | 81 | 7.9594 | 85 | 9.239 | 85 | 11.2399 | 89 | 12.1051 | 89 | 14.5209 | 95 | 16.1753 | 95 | 19.5367 | 105 | 23.0369 | 105 | 27.7953
70 | 0.53972 | 70 | 0.66506 | 72 | 1.1537 | 72 | 1.4009 | 76 | 2.8478 | 76 | 3.5002 | 78 | 3.9289 | 78 | 4.8007 | 80 | 5.1254 | 80 | 6.2296 | 82 | 6.4193 | 82 | 7.7642 | 86 | 9.043 | 86 | 10.9957 | 90 | 11.8762 | 90 | 14.2193 | 96 | 15.8896 | 96 | 19.1561 | 106 | 22.668 | 106 | 27.3045
71 | 0.52597 | 71 | 0.64679 | 73 | 1.125 | 73 | 1.3631 | 77 | 2.7803 | 77 | 3.409 | 79 | 3.838 | 79 | 4.6787 | 81 | 5.0094 | 81 | 6.075 | 83 | 6.2771 | 83 | 7.5761 | 87 | 8.8531 | 87 | 10.7595 | 91 | 11.6539 | 91 | 13.9271 | 97 | 15.6115 | 97 | 18.7866 | 107 | 22.3082 | 107 | 26.8269
72 | 0.51274 | 72 | 0.62928 | 74 | 1.0974 | 74 | 1.3268 | 78 | 2.7151 | 78 | 3.3213 | 80 | 3.7501 | 80 | 4.5612 | 82 | 4.8972 | 82 | 5.9261 | 84 | 6.1396 | 84 | 7.3947 | 88 | 8.6691 | 88 | 10.531 | 92 | 11.4379 | 92 | 13.6441 | 98 | 15.3408 | 98 | 18.428 | 108 | 21.9569 | 108 | 26.3619
73 | 0.5 | 73 | 0.61249 | 75 | 1.0708 | 75 | 1.292 | 79 | 2.6522 | 79 | 3.2369 | 81 | 3.6652 | 81 | 4.4481 | 83 | 4.7887 | 83 | 5.7826 | 85 | 5.8777 | 85 | 7.2197 | 89 | 8.4907 | 89 | 10.3098 | 93 | 11.2279 | 93 | 13.3698 | 99 | 15.0772 | 99 | 18.0798 | 109 | 21.6141 | 109 | 25.9092
74 | 0.48773 | 74 | 0.59637 | 76 | 1.0204 | 76 | 1.2585 | 80 | 2.5915 | 80 | 3.1557 | 82 | 3.5831 | 82 | 4.3391 | 84 | 4.6838 | 84 | 5.6442 | 86 | 5.753 | 86 | 7.0509 | 90 | 8.3178 | 90 | 10.0957 | 94 | 11.0238 | 94 | 13.1038 | 100 | 14.8205 | 100 | 17.7415 | 110 | 21.2795 | 110 | 25.4683
75 | 0.47591 | 75 | 0.58089 | 77 | 0.99654 | 77 | 1.2264 | 81 | 2.5328 | 81 | 3.0776 | 83 | 3.5037 | 83 | 4.2341 | 85 | 4.484 | 85 | 5.5107 | 87 | 5.6322 | 87 | 6.8879 | 91 | 8.1501 | 91 | 9.8788 | 95 | 10.6323 | 95 | 12.8459 | 101 | 14.5705 | 101 | 17.4129 | 111 | 20.9527 | 111 | 25.0387
76 | 0.45351 | 76 | 0.56602 | 78 | 0.9735 | 78 | 1.1954 | 82 | 2.4761 | 82 | 3.0023 | 84 | 3.427 | 84 | 4.1329 | 86 | 4.3889 | 86 | 5.3819 | 88 | 5.5151 | 88 | 6.7304 | 92 | 7.9874 | 92 | 9.6627 | 96 | 10.4445 | 96 | 12.5957 | 102 | 14.3268 | 102 | 17.0935 | 112 | 20.6335 | 112 | 24.6202
77 | 0.44291 | 77 | 0.55172 | 79 | 0.95125 | 79 | 1.1657 | 83 | 2.4213 | 83 | 2.9297 | 85 | 3.2808 | 85 | 4.0352 | 87 | 4.2967 | 87 | 5.2575 | 89 | 5.4017 | 89 | 6.5783 | 93 | 7.8294 | 93 | 9.4535 | 97 | 10.2617 | 97 | 12.3528 | 103 | 14.0893 | 103 | 16.783 | 113 | 20.3217 | 113 | 24.2123
78 | 0.43267 | 78 | 0.53797 | 80 | 0.92975 | 80 | 1.137 | 84 | 2.3682 | 84 | 2.8598 | 86 | 3.2112 | 86 | 3.9409 | 88 | 4.2074 | 88 | 5.1374 | 90 | 5.2916 | 90 | 6.4313 | 94 | 7.6761 | 94 | 9.251 | 98 | 10.0837 | 98 | 12.1171 | 104 | 13.8578 | 104 | 16.481 | 114 | 20.0171 | 114 | 23.8147
79 | 0.42278 | 79 | 0.52474 | 81 | 0.90898 | 81 | 1.1094 | 85 | 2.2672 | 85 | 2.7923 | 87 | 3.1437 | 87 | 3.85 | 89 | 4.1209 | 89 | 5.0213 | 91 | 5.1849 | 91 | 6.2891 | 95 | 7.3827 | 95 | 9.055 | 99 | 9.9035 | 99 | 11.8882 | 105 | 13.412 | 105 | 16.1873 | 115 | 19.4285 | 115 | 23.427
80 | 0.41322 | 80 | 0.512 | 82 | 0.88889 | 82 | 1.0828 | 86 | 2.2191 | 86 | 2.7271 | 88 | 3.0784 | 88 | 3.7621 | 90 | 4.0369 | 90 | 4.9092 | 92 | 5.0814 | 92 | 6.1516 | 96 | 7.2422 | 96 | 8.8651 | 100 | 9.7219 | 100 | 11.6659 | 106 | 13.1972 | 106 | 15.9016 | 116 | 19.1441 | 116 | 23.0489
81 | 0.40399 | 81 | 0.49973 | 83 | 0.86946 | 83 | 1.0571 | 87 | 2.1725 | 87 | 2.6642 | 89 | 3.0151 | 89 | 3.6772 | 91 | 3.9555 | 91 | 4.8007 | 93 | 4.9809 | 93 | 6.0185 | 97 | 7.1057 | 97 | 8.6811 | 101 | 9.5452 | 101 | 11.4499 | 107 | 12.9877 | 107 | 15.6235 | 117 | 18.866 | 117 | 22.68
82 | 0.39506 | 82 | 0.48791 | 84 | 0.85066 | 84 | 1.0324 | 88 | 2.1274 | 88 | 2.6035 | 90 | 2.9537 | 90 | 3.5951 | 92 | 3.8765 | 92 | 4.6958 | 94 | 4.8834 | 94 | 5.8897 | 98 | 6.973 | 98 | 8.5027 | 102 | 9.3733 | 102 | 11.2399 | 108 | 12.7832 | 108 | 15.3528 | 118 | 18.594 | 118 | 22.3202
83 | 0.38643 | 83 | 0.47651 | 85 | 0.81485 | 85 | 1.0085 | 89 | 2.0836 | 89 | 2.5448 | 91 | 2.8941 | 91 | 3.5157 | 93 | 3.7999 | 93 | 4.5943 | 95 | 4.6967 | 95 | 5.765 | 99 | 6.8439 | 99 | 8.3298 | 103 | 9.2059 | 103 | 11.0358 | 109 | 12.5837 | 109 | 15.0892 | 119 | 18.328 | 119 | 21.9689
84 | 0.37807 | 84 | 0.46551 | 86 | 0.79778 | 86 | 0.9855 | 90 | 2.0412 | 90 | 2.4881 | 92 | 2.8363 | 92 | 3.439 | 94 | 3.7255 | 94 | 4.496 | 96 | 4.6074 | 96 | 5.6442 | 100 | 6.7184 | 100 | 8.1621 | 104 | 9.043 | 104 | 10.8373 | 110 | 12.3888 | 110 | 14.8325 | 120 | 18.0678 | 120 | 21.6261
85 | 0.36215 | 85 | 0.45491 | 87 | 0.78125 | 87 | 0.96325 | 91 | 2 | 91 | 2.4333 | 93 | 2.7803 | 93 | 3.3647 | 95 | 3.5831 | 95 | 4.4009 | 97 | 4.5205 | 97 | 5.5271 | 101 | 6.5963 | 101 | 7.9993 | 105 | 8.7298 | 105 | 10.6443 | 111 | 12.1986 | 111 | 14.5825 | 121 | 17.8132 | 121 | 21.2915
86 | 0.35457 | 86 | 0.44467 | 88 | 0.76522 | 88 | 0.94175 | 92 | 1.9606 | 92 | 2.3802 | 94 | 2.7258 | 94 | 3.2928 | 96 | 3.5149 | 96 | 4.3087 | 98 | 4.4361 | 98 | 5.4136 | 102 | 6.4775 | 102 | 7.8414 | 106 | 8.5792 | 106 | 10.4565 | 112 | 12.0128 | 112 | 14.3388 | 122 | 17.564 | 122 | 20.9647
87 | 0.34722 | 87 | 0.43478 | 89 | 0.74969 | 89 | 0.92098 | 93 | 1.9223 | 93 | 2.3289 | 95 | 2.6216 | 95 | 3.2232 | 97 | 3.4487 | 97 | 4.2194 | 99 | 4.354 | 99 | 5.3036 | 103 | 6.3618 | 103 | 7.6881 | 107 | 8.4325 | 107 | 10.2737 | 113 | 11.8312 | 113 | 14.1013 | 123 | 17.3202 | 123 | 20.6455
88 | 0.3401 | 88 | 0.42522 | 90 | 0.73462 | 90 | 0.90089 | 94 | 1.8852 | 94 | 2.2792 | 96 | 2.5717 | 96 | 3.1557 | 98 | 3.3842 | 98 | 4.1329 | 100 | 4.2741 | 100 | 5.1969 | 104 | 6.2492 | 104 | 7.5393 | 108 | 8.2895 | 108 | 10.0957 | 114 | 11.6539 | 114 | 13.8698 | 124 | 17.0815 | 124 | 20.3337
89 | 0.33319 | 89 | 0.41599 | 91 | 0.72 | 91 | 0.88146 | 95 | 1.8141 | 95 | 2.2311 | 97 | 2.5232 | 97 | 3.0904 | 99 | 3.3216 | 99 | 4.0489 | 101 | 4.1964 | 101 | 5.0934 | 105 | 6.0328 | 105 | 7.3947 | 109 | 8.1501 | 109 | 9.9155 | 115 | 11.3112 | 115 | 13.6441 | 125 | 16.619 | 125 | 20.0291
90 | 0.3265 | 90 | 0.40706 | 92 | 0.70581 | 92 | 0.86266 | 96 | 1.78 | 96 | 2.1845 | 98 | 2.4761 | 98 | 3.0271 | 100 | 3.2607 | 100 | 3.9675 | 102 | 4.1209 | 102 | 4.993 | 106 | 5.9287 | 106 | 7.2542 | 110 | 8.0141 | 110 | 9.7339 | 116 | 11.1456 | 116 | 13.424 | 126 | 16.3949 | 126 | 19.7314
91 | 0.015625 | 91 | 0.39843 | 93 | 0.69204 | 93 | 0.84447 | 97 | 1.7469 | 97 | 2.1394 | 99 | 2.4303 | 99 | 2.9657 | 101 | 3.2014 | 101 | 3.8885 | 103 | 4.0473 | 103 | 4.8954 | 107 | 5.8273 | 107 | 7.1177 | 111 | 7.8816 | 111 | 9.5572 | 117 | 10.9837 | 117 | 13.2092 | 127 | 16.1753 | 127 | 19.4405
92 | 0.015625 | 92 | 0.39007 | 94 | 0.67867 | 94 | 0.82685 | 98 | 1.7147 | 98 | 2.0956 | 100 | 2.3857 | 100 | 2.9061 | 102 | 3.1437 | 102 | 3.8119 | 104 | 3.9756 | 104 | 4.8007 | 108 | 5.7285 | 108 | 6.985 | 112 | 7.7522 | 112 | 9.3853 | 118 | 10.8253 | 118 | 12.9997 | 128 | 15.9603 | 128 | 19.1561
93 | 0.015625 | 93 | 0.38198 | 95 | 0.65306 | 95 | 0.80978 | 99 | 1.6834 | 99 | 2.0532 | 101 | 2.3424 | 101 | 2.8483 | 103 | 3.0876 | 103 | 3.7375 | 105 | 3.838 | 105 | 4.7087 | 109 | 5.6322 | 109 | 6.8559 | 113 | 7.626 | 113 | 9.2179 | 119 | 10.6705 | 119 | 12.7952 | 129 | 15.7496 | 129 | 18.8779
94 | 0.015625 | 94 | 0.37415 | 96 | 0.6408 | 96 | 0.79325 | 100 | 1.6529 | 100 | 2.012 | 102 | 2.3002 | 102 | 2.7923 | 104 | 3.033 | 104 | 3.6653 | 106 | 3.7717 | 106 | 4.6194 | 110 | 5.5382 | 110 | 6.7304 | 114 | 7.5029 | 114 | 9.055 | 120 | 10.519 | 120 | 12.5957 | 130 | 15.5432 | 130 | 18.606
95 | 0.015625 | 95 | 0.36657 | 97 | 0.62888 | 97 | 0.77722 | 101 | 1.6232 | 101 | 1.9726 | 103 | 2.2591 | 103 | 2.7378 | 105 | 2.9279 | 105 | 3.5951 | 107 | 3.7073 | 107 | 4.5325 | 111 | 5.4466 | 111 | 6.6083 | 115 | 7.2653 | 115 | 8.8963 | 121 | 10.3707 | 121 | 12.4008 | 131 | 15.3408 | 131 | 18.34
96 | 0.015625 | 96 | 0.35922 | 98 | 0.61728 | 98 | 0.76169 | 102 | 1.5944 | 102 | 1.9343 | 104 | 2.2191 | 104 | 2.685 | 106 | 2.8774 | 106 | 3.5269 | 108 | 3.6444 | 108 | 4.4481 | 112 | 5.3572 | 112 | 6.4895 | 116 | 7.1508 | 116 | 8.7418 | 122 | 10.2257 | 122 | 12.2106 | 132 | 15.1425 | 132 | 18.0798
97 | 0.015625 | 97 | 0.3521 | 99 | 0.60601 | 99 | 0.74662 | 103 | 1.5663 | 103 | 1.8972 | 105 | 2.1423 | 105 | 2.6336 | 107 | 2.8282 | 107 | 3.4606 | 109 | 3.5831 | 109 | 4.366 | 113 | 5.27 | 113 | 6.3738 | 117 | 7.0389 | 117 | 8.5912 | 123 | 10.0837 | 123 | 12.0247 | 133 | 14.948 | 133 | 17.8252
98 | 0.015625 | 98 | 0.34519 | 100 | 0.59504 | 100 | 0.732 | 104 | 1.5389 | 104 | 1.8611 | 106 | 2.1053 | 106 | 2.5837 | 108 | 2.7803 | 108 | 3.3962 | 110 | 3.5233 | 110 | 4.2861 | 114 | 5.1849 | 114 | 6.2612 | 118 | 6.9295 | 118 | 8.4445 | 124 | 9.9405 | 124 | 11.8432 | 134 | 14.7574 | 134 | 17.576
99 | 0.015625 | 99 | 0.3385 | 101 | 0.58437 | 101 | 0.71781 | 105 | 1.4863 | 105 | 1.8261 | 107 | 2.0693 | 107 | 2.5353 | 109 | 2.7335 | 109 | 3.3336 | 111 | 3.465 | 111 | 4.2085 | 115 | 5.0208 | 115 | 6.1516 | 119 | 6.8228 | 119 | 8.3015 | 125 | 9.6507 | 125 | 11.6659 | 135 | 14.5705 | 135 | 17.3322
100 | 0.015625 | 100 | 0.03334 | 102 | 0.57398 | 102 | 0.70404 | 106 | 1.461 | 106 | 1.792 | 108 | 2.0342 | 108 | 2.4881 | 110 | 2.6879 | 110 | 3.2727 | 112 | 3.4082 | 112 | 4.1329 | 116 | 4.9416 | 116 | 6.0448 | 120 | 6.7184 | 120 | 8.1621 | 126 | 9.5105 | 126 | 11.4926 | 136 | 14.2073 | 136 | 17.0935
453 | 0.015625 | 453 | 0.03334 | 103 | 0.56387 | 103 | 0.69067 | 107 | 1.4364 | 107 | 1.7589 | 109 | 2 | 109 | 2.4423 | 111 | 2.6434 | 111 | 3.2134 | 113 | 3.3527 | 113 | 4.0593 | 117 | 4.8643 | 117 | 5.9407 | 121 | 6.6164 | 121 | 8.0261 | 127 | 9.3733 | 127 | 11.3232 | 137 | 14.0309 | 137 | 16.8598
454 | 0.011042 | 454 | 0.03334 | 104 | 0.55402 | 104 | 0.67768 | 108 | 1.4123 | 108 | 1.7267 | 110 | 1.9671 | 110 | 2.3977 | 112 | 2.6001 | 112 | 3.1557 | 114 | 3.2986 | 114 | 3.9876 | 118 | 4.7887 | 118 | 5.8393 | 122 | 6.5167 | 122 | 7.8936 | 128 | 9.239 | 128 | 11.1576 | 138 | 13.8578 | 138 | 16.631
455 | 0.001 | 455 | 0.03334 | 105 | 0.53508 | 105 | 0.66506 | 109 | 1.3889 | 109 | 1.6954 | 111 | 1.935 | 111 | 2.3544 | 113 | 2.5577 | 113 | 3.0996 | 115 | 3.1941 | 115 | 3.9179 | 119 | 4.7149 | 119 | 5.7405 | 123 | 6.4193 | 123 | 7.7642 | 129 | 9.1076 | 129 | 10.9957 | 139 | 13.688 | 139 | 16.4068
500 | 0.001 | 500 | 0.03334 | 106 | 0.52597 | 106 | 0.6528 | 110 | 1.366 | 110 | 1.6649 | 112 | 1.9036 | 112 | 2.3122 | 114 | 2.5164 | 114 | 3.045 | 116 | 3.1437 | 116 | 3.85 | 120 | 4.6428 | 120 | 5.6442 | 124 | 6.3239 | 124 | 7.638 | 130 | 8.979 | 130 | 10.8373 | 140 | 13.5213 | 140 | 16.1873
501 | 0.001 | 501 | 0.01667 | 107 | 0.51709 | 107 | 0.64088 | 111 | 1.3437 | 111 | 1.6352 | 113 | 1.8731 | 113 | 2.2711 | 115 | 2.4368 | 115 | 2.9918 | 117 | 3.0946 | 117 | 3.7837 | 121 | 4.5723 | 121 | 5.5502 | 125 | 6.1396 | 125 | 7.5149 | 131 | 8.8531 | 131 | 10.6825 | 141 | 13.3578 | 141 | 15.9723
6300 | 0.001 | 6300 | 0.01667 | 108 | 0.50844 | 108 | 0.62928 | 112 | 1.322 | 112 | 1.6064 | 114 | 1.8432 | 114 | 2.2311 | 116 | 2.3983 | 116 | 2.9399 | 118 | 3.0465 | 118 | 3.7193 | 122 | 4.5034 | 122 | 5.4586 | 126 | 6.0504 | 126 | 7.3947 | 132 | 8.7298 | 132 | 10.531 | 142 | 13.1972 | 142 | 15.7616
|  |  |  | 109 | 0.5 | 109 | 0.61801 | 113 | 1.3007 | 113 | 1.5783 | 115 | 1.7856 | 115 | 2.1922 | 117 | 2.3608 | 117 | 2.8894 | 119 | 2.9996 | 119 | 3.6564 | 123 | 4.4361 | 123 | 5.3692 | 127 | 5.9631 | 127 | 7.2774 | 133 | 8.609 | 133 | 10.3827 | 143 | 13.0396 | 143 | 15.5551
|  |  |  | 110 | 0.49177 | 110 | 0.60704 | 114 | 1.28 | 114 | 1.5509 | 116 | 1.7578 | 116 | 2.1543 | 118 | 2.3241 | 118 | 2.8402 | 120 | 2.9537 | 120 | 3.5951 | 124 | 4.3702 | 124 | 5.282 | 128 | 5.8777 | 128 | 7.1628 | 134 | 8.4907 | 134 | 10.2377 | 144 | 12.8849 | 144 | 15.3528
|  |  |  | 111 | 0.48374 | 111 | 0.59637 | 115 | 1.24 | 115 | 1.5243 | 117 | 1.7307 | 117 | 2.1173 | 119 | 2.2883 | 119 | 2.7923 | 121 | 2.9088 | 121 | 3.5353 | 125 | 4.2428 | 125 | 5.1969 | 129 | 5.7941 | 129 | 7.0509 | 135 | 8.3749 | 135 | 10.0957 | 145 | 12.5837 | 145 | 15.1545
|  |  |  | 112 | 0.47591 | 112 | 0.58598 | 116 | 1.2207 | 116 | 1.4983 | 118 | 1.7041 | 118 | 2.0813 | 120 | 2.2533 | 120 | 2.7455 | 122 | 2.865 | 122 | 3.477 | 126 | 4.1812 | 126 | 5.1139 | 130 | 5.7123 | 130 | 6.9416 | 136 | 8.1501 | 136 | 9.9525 | 146 | 12.4371 | 146 | 14.96
|  |  |  | 113 | 0.46826 | 113 | 0.57587 | 117 | 1.2019 | 117 | 1.473 | 119 | 1.6782 | 119 | 2.0462 | 121 | 2.2191 | 121 | 2.6999 | 123 | 2.8222 | 123 | 3.4202 | 127 | 4.1209 | 127 | 5.0328 | 131 | 5.6322 | 131 | 6.8348 | 137 | 8.0411 | 137 | 9.806 | 147 | 12.2931 | 147 | 14.7694
|  |  |  | 114 | 0.4608 | 114 | 0.56602 | 118 | 1.1834 | 118 | 1.4484 | 120 | 1.6529 | 120 | 2.012 | 122 | 2.1857 | 122 | 2.6554 | 124 | 2.7803 | 124 | 3.3647 | 128 | 4.0618 | 128 | 4.9536 | 132 | 5.5537 | 132 | 6.7304 | 138 | 7.9342 | 138 | 9.6627 | 148 | 12.1517 | 148 | 14.5825
|  |  |  | 115 | 0.4464 | 115 | 0.55642 | 119 | 1.1654 | 119 | 1.4243 | 121 | 1.6281 | 121 | 1.9791 | 123 | 2.153 | 123 | 2.6121 | 125 | 2.6992 | 125 | 3.3106 | 129 | 4.0041 | 129 | 4.8763 | 133 | 5.4769 | 133 | 6.6284 | 139 | 7.8294 | 139 | 9.5225 | 149 | 12.0128 | 149 | 14.3991
|  |  |  | 116 | 0.43945 | 116 | 0.54708 | 120 | 1.1478 | 120 | 1.4009 | 122 | 1.6039 | 122 | 1.947 | 124 | 2.121 | 124 | 2.5697 | 126 | 2.66 | 126 | 3.2577 | 130 | 3.9475 | 130 | 4.8007 | 134 | 5.4017 | 134 | 6.5287 | 140 | 7.7267 | 140 | 9.3853 | 150 | 11.8762 | 150 | 14.2193
|  |  |  | 117 | 0.43267 | 117 | 0.53797 | 121 | 1.1306 | 121 | 1.378 | 123 | 1.5802 | 123 | 1.9156 | 125 | 2.0592 | 125 | 2.5284 | 127 | 2.6216 | 127 | 3.2061 | 131 | 3.8922 | 131 | 4.7269 | 135 | 5.3279 | 135 | 6.4313 | 141 | 7.626 | 141 | 9.251 | 151 | 11.742 | 151 | 14.0429
|  |  |  | 118 | 0.42604 | 118 | 0.52909 | 122 | 1.1138 | 122 | 1.3557 | 124 | 1.5571 | 124 | 1.885 | 126 | 2.0293 | 126 | 2.4881 | 128 | 2.5841 | 128 | 3.1557 | 132 | 3.838 | 132 | 4.6548 | 136 | 5.1849 | 136 | 6.336 | 142 | 7.5273 | 142 | 9.1196 | 152 | 11.6102 | 152 | 13.8698
|  |  |  | 119 | 0.41956 | 119 | 0.52044 | 123 | 1.0974 | 123 | 1.334 | 125 | 1.5123 | 125 | 1.8552 | 127 | 2 | 127 | 2.4488 | 129 | 2.5473 | 129 | 3.1066 | 133 | 3.7849 | 133 | 4.5843 | 137 | 5.1156 | 137 | 6.2428 | 143 | 7.4304 | 143 | 8.991 | 153 | 11.4806 | 153 | 13.7
|  |  |  | 120 | 0.41322 | 120 | 0.512 | 124 | 1.0813 | 124 | 1.3127 | 126 | 1.4906 | 126 | 1.8261 | 128 | 1.9717 | 128 | 2.4103 | 130 | 2.5113 | 130 | 3.0585 | 134 | 3.7329 | 134 | 4.5154 | 138 | 5.0476 | 138 | 6.1516 | 144 | 7.3354 | 144 | 8.8651 | 154 | 11.3532 | 154 | 13.5334
|  |  |  | 121 | 0.40703 | 121 | 0.50377 | 125 | 1.0502 | 125 | 1.292 | 127 | 1.4694 | 127 | 1.7976 | 129 | 1.9441 | 129 | 2.3728 | 131 | 2.4761 | 131 | 3.0116 | 135 | 3.6819 | 135 | 4.4481 | 139 | 4.9809 | 139 | 6.0624 | 145 | 7.1508 | 145 | 8.7418 | 155 | 11.2279 | 155 | 13.3698
|  |  |  | 122 | 0.40098 | 122 | 0.49574 | 126 | 1.0351 | 126 | 1.2718 | 128 | 1.4486 | 128 | 1.7698 | 130 | 1.917 | 130 | 2.3361 | 132 | 2.4416 | 132 | 2.9657 | 136 | 3.5831 | 136 | 4.3822 | 140 | 4.9156 | 140 | 5.9751 | 146 | 7.061 | 146 | 8.621 | 156 | 10.9837 | 156 | 13.2092
|  |  |  | 123 | 0.39506 | 123 | 0.48791 | 127 | 1.0204 | 127 | 1.252 | 129 | 1.4283 | 129 | 1.7427 | 131 | 1.8904 | 131 | 2.3003 | 133 | 2.4079 | 133 | 2.9208 | 137 | 3.5352 | 137 | 4.3178 | 141 | 4.8515 | 141 | 5.8897 | 147 | 6.973 | 147 | 8.5027 | 157 | 10.8646 | 157 | 13.0516
|  |  |  | 124 | 0.38927 | 124 | 0.48026 | 128 | 1.006 | 128 | 1.2327 | 130 | 1.4084 | 130 | 1.7161 | 132 | 1.8644 | 132 | 2.2653 | 134 | 2.3748 | 134 | 2.877 | 138 | 3.4882 | 138 | 4.2548 | 142 | 4.7887 | 142 | 5.8061 | 148 | 6.8865 | 148 | 8.3869 | 158 | 10.7475 | 158 | 12.8969
|  |  |  | 125 | 0.37807 | 125 | 0.4728 | 129 | 0.99187 | 129 | 1.2139 | 131 | 1.3889 | 131 | 1.6902 | 133 | 1.839 | 133 | 2.2311 | 135 | 2.3424 | 135 | 2.8342 | 139 | 3.4421 | 139 | 4.1932 | 143 | 4.7271 | 143 | 5.7243 | 149 | 6.8017 | 149 | 8.2733 | 159 | 10.6323 | 159 | 12.7449
|  |  |  | 126 | 0.37265 | 126 | 0.46551 | 130 | 0.97804 | 130 | 1.1954 | 132 | 1.3698 | 132 | 1.6649 | 134 | 1.8141 | 134 | 2.1977 | 136 | 2.2795 | 136 | 2.7923 | 140 | 3.397 | 140 | 4.1329 | 144 | 4.6667 | 144 | 5.6442 | 150 | 6.7184 | 150 | 8.1621 | 160 | 10.519 | 160 | 12.5957
|  |  |  | 127 | 0.36735 | 127 | 0.4584 | 131 | 0.96451 | 131 | 1.1774 | 133 | 1.3511 | 133 | 1.6401 | 135 | 1.7896 | 135 | 2.165 | 137 | 2.249 | 137 | 2.7513 | 141 | 3.3527 | 141 | 4.0738 | 145 | 4.5492 | 145 | 5.5657 | 151 | 6.6366 | 151 | 8.0531 | 161 | 10.4075 | 161 | 12.4491
|  |  |  | 128 | 0.36215 | 128 | 0.45145 | 132 | 0.95125 | 132 | 1.1598 | 134 | 1.3328 | 134 | 1.6159 | 136 | 1.7422 | 136 | 2.133 | 138 | 2.2191 | 138 | 2.7112 | 142 | 3.3093 | 142 | 4.0161 | 146 | 4.4921 | 146 | 5.4889 | 152 | 6.5563 | 152 | 7.9462 | 162 | 10.2978 | 162 | 12.3051
|  |  |  | 129 | 0.35707 | 129 | 0.44467 | 133 | 0.93826 | 133 | 1.1426 | 135 | 1.3148 | 135 | 1.5922 | 137 | 1.7192 | 137 | 2.1018 | 139 | 2.1898 | 139 | 2.672 | 143 | 3.2667 | 143 | 3.9595 | 147 | 4.4361 | 147 | 5.4136 | 153 | 6.4775 | 153 | 7.8414 | 163 | 10.1899 | 163 | 12.1637
|  |  |  | 130 | 0.3521 | 130 | 0.43804 | 134 | 0.92554 | 134 | 1.1258 | 136 | 1.28 | 136 | 1.5691 | 138 | 1.6967 | 138 | 2.0712 | 140 | 2.1611 | 140 | 2.6336 | 144 | 3.2249 | 144 | 3.9042 | 148 | 4.3811 | 148 | 5.3399 | 154 | 6.4 | 154 | 7.7387 | 164 | 10.0837 | 164 | 12.0247
|  |  |  | 131 | 0.34722 | 131 | 0.43156 | 135 | 0.91308 | 135 | 1.1094 | 137 | 1.2631 | 137 | 1.5465 | 139 | 1.6746 | 139 | 2.0413 | 141 | 2.1329 | 141 | 2.5961 | 145 | 3.1437 | 145 | 3.85 | 149 | 4.3271 | 149 | 5.2677 | 155 | 6.3239 | 155 | 7.638 | 165 | 9.8668 | 165 | 11.8882
|  |  |  | 132 | 0.34245 | 132 | 0.42522 | 136 | 0.88889 | 136 | 1.0933 | 138 | 1.2465 | 138 | 1.5243 | 140 | 1.6529 | 140 | 2.012 | 142 | 2.1053 | 142 | 2.5593 | 146 | 3.1043 | 146 | 3.7969 | 150 | 4.2741 | 150 | 5.1969 | 156 | 6.1758 | 156 | 7.5393 | 166 | 9.7578 | 166 | 11.754
|  |  |  | 133 | 0.33777 | 133 | 0.41903 | 137 | 0.87715 | 137 | 1.0776 | 139 | 1.2303 | 139 | 1.5026 | 141 | 1.6316 | 141 | 1.9837 | 143 | 2.0782 | 143 | 2.5233 | 147 | 3.0656 | 147 | 3.7449 | 151 | 4.2221 | 151 | 5.1276 | 157 | 6.1037 | 157 | 7.4424 | 167 | 9.6507 | 167 | 11.6222
|  |  |  | 134 | 0.33319 | 134 | 0.41298 | 138 | 0.86565 | 138 | 1.0622 | 140 | 1.2144 | 140 | 1.4814 | 142 | 1.6108 | 142 | 1.9561 | 144 | 2.0516 | 144 | 2.4881 | 148 | 3.0276 | 148 | 3.6939 | 152 | 4.171 | 152 | 5.0596 | 158 | 6.0328 | 158 | 7.3474 | 168 | 9.5452 | 168 | 11.4926
|  |  |  | 135 | 0.32871 | 135 | 0.40706 | 139 | 0.85437 | 139 | 1.0471 | 141 | 1.1987 | 141 | 1.4606 | 143 | 1.5903 | 143 | 1.929 | 145 | 2 | 145 | 2.4536 | 149 | 2.9903 | 149 | 3.644 | 153 | 4.1209 | 153 | 4.993 | 159 | 5.9631 | 159 | 7.2542 | 169 | 9.4415 | 169 | 11.3652
|  |  |  | 136 | 0.015625 | 136 | 0.40127 | 140 | 0.84331 | 140 | 1.0324 | 142 | 1.1834 | 142 | 1.4403 | 144 | 1.5703 | 144 | 1.9024 | 146 | 1.9752 | 146 | 2.4199 | 150 | 2.9537 | 150 | 3.5951 | 154 | 4.0716 | 154 | 4.9276 | 160 | 5.8946 | 160 | 7.1628 | 170 | 9.3394 | 170 | 11.2399
|  |  |  | 137 | 0.015625 | 137 | 0.39561 | 141 | 0.83247 | 141 | 1.018 | 143 | 1.1684 | 143 | 1.4204 | 145 | 1.5312 | 145 | 1.8764 | 147 | 1.9509 | 147 | 2.3868 | 151 | 2.9177 | 151 | 3.5472 | 155 | 4.0232 | 155 | 4.8636 | 161 | 5.8273 | 161 | 7.073 | 171 | 9.239 | 171 | 11.1168
|  |  |  | 138 | 0.015625 | 138 | 0.39007 | 142 | 0.82183 | 142 | 1.0039 | 144 | 1.1537 | 144 | 1.4009 | 146 | 1.5123 | 146 | 1.851 | 148 | 1.9271 | 148 | 2.3544 | 152 | 2.8824 | 152 | 3.5002 | 156 | 3.9289 | 156 | 4.8007 | 162 | 5.7612 | 162 | 6.985 | 172 | 9.1402 | 172 | 10.9957
|  |  |  | 139 | 0.015625 | 139 | 0.38465 | 143 | 0.81139 | 143 | 0.99004 | 145 | 1.125 | 145 | 1.3818 | 147 | 1.4937 | 147 | 1.8261 | 149 | 1.9036 | 149 | 2.3226 | 153 | 2.8478 | 153 | 3.4541 | 157 | 3.883 | 157 | 4.7391 | 163 | 5.6961 | 163 | 6.8985 | 173 | 9.043 | 173 | 10.8766
|  |  |  | 140 | 0.015625 | 140 | 0.37935 | 144 | 0.80115 | 144 | 0.97651 | 146 | 1.1111 | 146 | 1.3631 | 148 | 1.4754 | 148 | 1.8016 | 150 | 1.8806 | 150 | 2.2915 | 154 | 2.8137 | 154 | 3.409 | 158 | 3.838 | 158 | 4.6787 | 164 | 5.6322 | 164 | 6.8137 | 174 | 8.9473 | 174 | 10.7595
|  |  |  | 141 | 0.015625 | 141 | 0.37415 | 145 | 0.78125 | 145 | 0.96325 | 147 | 1.0974 | 147 | 1.3448 | 149 | 1.4575 | 149 | 1.7777 | 151 | 1.858 | 151 | 2.261 | 155 | 2.7803 | 155 | 3.3647 | 159 | 3.7936 | 159 | 4.6194 | 165 | 5.5074 | 165 | 6.7304 | 175 | 8.7604 | 175 | 10.6443
|  |  |  | 142 | 0.015625 | 142 | 0.36907 | 146 | 0.77158 | 146 | 0.95026 | 148 | 1.084 | 148 | 1.3268 | 150 | 1.4399 | 150 | 1.7542 | 152 | 1.8358 | 152 | 2.2311 | 156 | 2.7151 | 156 | 3.3213 | 160 | 3.7501 | 160 | 4.5612 | 166 | 5.4466 | 166 | 6.6486 | 176 | 8.6691 | 176 | 10.531
|  |  |  | 143 | 0.015625 | 143 | 0.3641 | 147 | 0.76208 | 147 | 0.93754 | 149 | 1.0708 | 149 | 1.3092 | 151 | 1.4226 | 151 | 1.7312 | 153 | 1.8141 | 153 | 2.2018 | 157 | 2.6834 | 157 | 3.2787 | 161 | 3.7073 | 161 | 4.5041 | 167 | 5.3868 | 167 | 6.5683 | 177 | 8.5792 | 177 | 10.4195
|  |  |  | 144 | 0.015625 | 144 | 0.35922 | 148 | 0.75276 | 148 | 0.92508 | 150 | 1.0578 | 150 | 1.292 | 152 | 1.4056 | 152 | 1.7087 | 154 | 1.7927 | 154 | 2.1731 | 158 | 2.6522 | 158 | 3.2369 | 162 | 3.6652 | 162 | 4.4481 | 168 | 5.3279 | 168 | 6.4895 | 178 | 8.4907 | 178 | 10.3098
|  |  |  | 145 | 0.015625 | 145 | 0.35445 | 149 | 0.7436 | 149 | 0.91286 | 151 | 1.0451 | 151 | 1.2751 | 153 | 1.3889 | 153 | 1.6866 | 155 | 1.7716 | 155 | 2.1449 | 159 | 2.6216 | 159 | 3.196 | 163 | 3.6238 | 163 | 4.3931 | 169 | 5.27 | 169 | 6.412 | 179 | 8.4036 | 179 | 10.2019
|  |  |  | 146 | 0.015625 | 146 | 0.34977 | 150 | 0.73462 | 150 | 0.90089 | 152 | 1.0327 | 152 | 1.2585 | 154 | 1.3725 | 154 | 1.6649 | 156 | 1.7307 | 156 | 2.1173 | 160 | 2.5915 | 160 | 3.1557 | 164 | 3.5831 | 164 | 4.3391 | 170 | 5.2131 | 170 | 6.336 | 180 | 8.3178 | 180 | 10.0957
|  |  |  | 147 | 0.015625 | 147 | 0.34519 | 151 | 0.72579 | 151 | 0.88915 | 153 | 1.0204 | 153 | 1.2423 | 155 | 1.3564 | 155 | 1.6436 | 157 | 1.7107 | 157 | 2.0902 | 161 | 2.5619 | 161 | 3.1163 | 165 | 3.5037 | 165 | 4.2861 | 171 | 5.157 | 171 | 6.2612 | 181 | 8.2333 | 181 | 9.9896
|  |  |  | 148 | 0.015625 | 148 | 0.34071 | 152 | 0.71713 | 152 | 0.87765 | 154 | 1.0084 | 154 | 1.2264 | 156 | 1.325 | 156 | 1.6228 | 158 | 1.6911 | 158 | 2.0636 | 162 | 2.5328 | 162 | 3.0776 | 166 | 3.465 | 166 | 4.2341 | 172 | 5.1019 | 172 | 6.1878 | 182 | 8.1501 | 182 | 9.8788
|  |  |  | 149 | 0.015625 | 149 | 0.33631 | 153 | 0.70862 | 153 | 0.86637 | 155 | 0.99654 | 155 | 1.2107 | 157 | 1.3098 | 157 | 1.6023 | 159 | 1.6718 | 159 | 2.0376 | 163 | 2.5042 | 163 | 3.0396 | 167 | 3.427 | 167 | 4.183 | 173 | 5.0476 | 173 | 6.1157 | 183 | 8.0681 | 183 | 9.7698
|  |  |  | 150 | 0.015625 | 150 | 0.03334 | 154 | 0.70026 | 154 | 0.85531 | 156 | 0.9735 | 156 | 1.1954 | 158 | 1.2948 | 158 | 1.5823 | 160 | 1.6529 | 160 | 2.012 | 164 | 2.4761 | 164 | 3.0023 | 168 | 3.3895 | 168 | 4.1329 | 174 | 4.9942 | 174 | 6.0448 | 184 | 7.9874 | 184 | 9.6627
|  |  |  | 453 | 0.015625 | 453 | 0.03334 | 155 | 0.69204 | 155 | 0.84447 | 157 | 0.96228 | 157 | 1.1804 | 159 | 1.28 | 159 | 1.5626 | 161 | 1.6343 | 161 | 1.9872 | 165 | 2.4213 | 165 | 2.9657 | 169 | 3.3527 | 169 | 4.0836 | 175 | 4.8898 | 175 | 5.9751 | 185 | 7.8294 | 185 | 9.5572
|  |  |  | 454 | 0.011042 | 454 | 0.03334 | 156 | 0.67604 | 156 | 0.83383 | 158 | 0.95125 | 158 | 1.1657 | 160 | 1.2655 | 160 | 1.5433 | 162 | 1.616 | 162 | 1.9629 | 166 | 2.3945 | 166 | 2.9297 | 170 | 3.3165 | 170 | 4.0352 | 176 | 4.8389 | 176 | 5.9066 | 186 | 7.7522 | 186 | 9.4535
|  |  |  | 455 | 0.001 | 455 | 0.03334 | 157 | 0.66825 | 157 | 0.82339 | 159 | 0.94041 | 159 | 1.1512 | 161 | 1.2512 | 161 | 1.5243 | 163 | 1.5979 | 163 | 1.9391 | 167 | 2.3682 | 167 | 2.8944 | 171 | 3.2808 | 171 | 3.9876 | 177 | 4.7887 | 177 | 5.8393 | 187 | 7.6761 | 187 | 9.3514
|  |  |  | 500 | 0.001 | 500 | 0.03334 | 158 | 0.66059 | 158 | 0.81315 | 160 | 0.92975 | 160 | 1.137 | 162 | 1.2372 | 162 | 1.5057 | 164 | 1.5802 | 164 | 1.9156 | 168 | 2.3424 | 168 | 2.8598 | 172 | 3.2457 | 172 | 3.9409 | 178 | 4.7393 | 178 | 5.7732 | 188 | 7.6012 | 188 | 9.251
|  |  |  | 501 | 0.001 | 501 | 0.01667 | 159 | 0.65306 | 159 | 0.80311 | 161 | 0.91928 | 161 | 1.1231 | 163 | 1.2234 | 163 | 1.4874 | 165 | 1.5457 | 165 | 1.8926 | 169 | 2.3169 | 169 | 2.8257 | 173 | 3.2112 | 173 | 3.895 | 179 | 4.6907 | 179 | 5.7081 | 189 | 7.5273 | 189 | 9.1522
|  |  |  | 6300 | 0.001 | 6300 | 0.01667 | 160 | 0.64566 | 160 | 0.79325 | 162 | 0.90898 | 162 | 1.1094 | 164 | 1.2099 | 164 | 1.4695 | 166 | 1.5289 | 166 | 1.87 | 170 | 2.2919 | 170 | 2.7923 | 174 | 3.1772 | 174 | 3.85 | 180 | 4.6428 | 180 | 5.6442 | 190 | 7.4545 | 190 | 9.055
[8 empty] | 161 | 0.63839 | 161 | 0.78358 | 163 | 0.89885 | 163 | 1.096 | 165 | 1.1834 | 165 | 1.4519 | 167 | 1.5123 | 167 | 1.8478 | 171 | 2.2672 | 171 | 2.7594 | 175 | 3.1108 | 175 | 3.8056 | 181 | 4.5956 | 181 | 5.5813 | 191 | 7.3827 | 191 | 8.9593
[8 empty] | 162 | 0.63123 | 162 | 0.77408 | 164 | 0.88889 | 164 | 1.0828 | 166 | 1.1705 | 166 | 1.4346 | 168 | 1.496 | 168 | 1.8261 | 172 | 2.243 | 172 | 2.7271 | 176 | 3.0784 | 176 | 3.7621 | 182 | 4.5492 | 182 | 5.5194 | 192 | 7.312 | 192 | 8.8651
[8 empty] | 163 | 0.6242 | 163 | 0.76476 | 165 | 0.86946 | 165 | 1.0698 | 167 | 1.1578 | 167 | 1.4176 | 169 | 1.4799 | 169 | 1.8047 | 173 | 2.2191 | 173 | 2.6954 | 177 | 3.0465 | 177 | 3.7193 | 183 | 4.5034 | 183 | 5.4586 | 193 | 7.2422 | 193 | 8.7724
[8 empty] | 164 | 0.61728 | 164 | 0.7556 | 166 | 0.85998 | 166 | 1.0571 | 168 | 1.1454 | 168 | 1.4009 | 170 | 1.4642 | 170 | 1.7836 | 174 | 2.1956 | 174 | 2.6642 | 178 | 3.0151 | 178 | 3.6772 | 184 | 4.4584 | 184 | 5.3988 | 194 | 7.1735 | 194 | 8.6811
[8 empty] | 165 | 0.60379 | 165 | 0.74662 | 167 | 0.85066 | 167 | 1.0447 | 169 | 1.1331 | 169 | 1.3845 | 171 | 1.4486 | 171 | 1.763 | 175 | 2.1498 | 175 | 2.6336 | 179 | 2.9841 | 179 | 3.6358 | 185 | 4.3702 | 185 | 5.3399 | 195 | 7.0389 | 195 | 8.5912
[8 empty] | 166 | 0.59721 | 166 | 0.73779 | 168 | 0.84149 | 168 | 1.0324 | 170 | 1.121 | 170 | 1.3684 | 172 | 1.4333 | 172 | 1.7427 | 176 | 2.1274 | 176 | 2.6035 | 180 | 2.9537 | 180 | 3.5951 | 186 | 4.3271 | 186 | 5.282 | 196 | 6.973 | 196 | 8.5027
[8 empty] | 167 | 0.59074 | 167 | 0.72913 | 169 | 0.83247 | 169 | 1.0204 | 171 | 1.1091 | 171 | 1.3526 | 173 | 1.4183 | 173 | 1.7227 | 177 | 2.1053 | 177 | 2.5739 | 181 | 2.9237 | 181 | 3.5551 | 187 | 4.2847 | 187 | 5.2251 | 197 | 6.908 | 197 | 8.4156
[8 empty] | 168 | 0.58437 | 168 | 0.72062 | 170 | 0.82359 | 170 | 1.0085 | 172 | 1.0974 | 172 | 1.337 | 174 | 1.4035 | 174 | 1.7031 | 178 | 2.0836 | 178 | 2.5448 | 182 | 2.8941 | 182 | 3.5157 | 188 | 4.2428 | 188 | 5.169 | 198 | 6.8439 | 198 | 8.3298
[8 empty] | 169 | 0.5781 | 169 | 0.71226 | 171 | 0.81485 | 171 | 0.99692 | 173 | 1.0859 | 173 | 1.3218 | 175 | 1.3745 | 175 | 1.6838 | 179 | 2.0622 | 179 | 2.5162 | 183 | 2.865 | 183 | 3.477 | 189 | 4.2016 | 189 | 5.1139 | 199 | 6.7807 | 199 | 8.2453
[8 empty] | 170 | 0.57194 | 170 | 0.70404 | 172 | 0.80625 | 172 | 0.9855 | 174 | 1.0745 | 174 | 1.3068 | 176 | 1.3604 | 176 | 1.6649 | 180 | 2.0412 | 180 | 2.4881 | 184 | 2.8363 | 184 | 3.439 | 190 | 4.1609 | 190 | 5.0596 | 200 | 6.7184 | 200 | 8.1621
[8 empty] | 171 | 0.56587 | 171 | 0.69597 | 173 | 0.79778 | 173 | 0.97428 | 175 | 1.0524 | 175 | 1.292 | 177 | 1.3465 | 177 | 1.6463 | 181 | 2.0204 | 181 | 2.4605 | 185 | 2.7803 | 185 | 3.4015 | 191 | 4.1209 | 191 | 5.0062 | 201 | 6.6569 | 201 | 8.0801
[8 empty] | 172 | 0.55989 | 172 | 0.68804 | 174 | 0.78945 | 174 | 0.96325 | 176 | 1.0416 | 176 | 1.2775 | 178 | 1.3328 | 178 | 1.628 | 182 | 2 | 182 | 2.4333 | 186 | 2.7528 | 186 | 3.3647 | 192 | 4.0814 | 192 | 4.9536 | 202 | 6.5963 | 202 | 7.9993
[8 empty] | 173 | 0.55402 | 173 | 0.68025 | 175 | 0.77318 | 175 | 0.95241 | 177 | 1.0309 | 177 | 1.2632 | 179 | 1.3193 | 179 | 1.6099 | 183 | 1.9802 | 183 | 2.4065 | 187 | 2.7258 | 187 | 3.3285 | 193 | 4.0424 | 193 | 4.9018 | 203 | 6.5365 | 203 | 7.9198
[8 empty] | 174 | 0.54823 | 174 | 0.67259 | 176 | 0.76522 | 176 | 0.94175 | 178 | 1.0204 | 178 | 1.2492 | 180 | 1.306 | 180 | 1.5922 | 184 | 1.9606 | 184 | 2.3802 | 188 | 2.6992 | 188 | 3.2928 | 194 | 4.0041 | 194 | 4.8509 | 204 | 6.4775 | 204 | 7.8414
[8 empty] | 175 | 0.53693 | 175 | 0.66506 | 177 | 0.7574 | 177 | 0.93128 | 179 | 1.0101 | 179 | 1.2354 | 181 | 1.2929 | 181 | 1.5748 | 185 | 1.9223 | 185 | 2.3544 | 189 | 2.673 | 189 | 3.2577 | 195 | 3.9289 | 195 | 4.8007 | 205 | 6.3618 | 205 | 7.7642
[8 empty] | 176 | 0.53141 | 176 | 0.65766 | 178 | 0.74969 | 178 | 0.92098 | 180 | 0.9999 | 180 | 1.2219 | 182 | 1.28 | 182 | 1.5577 | 186 | 1.9036 | 186 | 2.3289 | 190 | 2.6471 | 190 | 3.2232 | 196 | 3.8922 | 196 | 4.7513 | 206 | 6.3052 | 206 | 7.6881
[8 empty] | 177 | 0.52597 | 177 | 0.65039 | 179 | 0.7421 | 179 | 0.91085 | 181 | 0.98987 | 181 | 1.2085 | 183 | 1.2673 | 183 | 1.5409 | 187 | 1.8852 | 187 | 2.3039 | 191 | 2.6216 | 191 | 3.1892 | 197 | 3.8559 | 197 | 4.7027 | 207 | 6.2492 | 207 | 7.6132
[8 empty] | 178 | 0.52062 | 178 | 0.64323 | 180 | 0.73462 | 180 | 0.90089 | 182 | 0.98 | 182 | 1.1954 | 184 | 1.2548 | 184 | 1.5243 | 188 | 1.867 | 188 | 2.2792 | 192 | 2.5965 | 192 | 3.1557 | 198 | 3.8201 | 198 | 4.6548 | 208 | 6.194 | 208 | 7.5393
[8 empty] | 179 | 0.51534 | 179 | 0.6362 | 181 | 0.72725 | 181 | 0.89109 | 183 | 0.97027 | 183 | 1.1825 | 185 | 1.2303 | 185 | 1.508 | 189 | 1.8491 | 189 | 2.255 | 193 | 2.5717 | 193 | 3.1228 | 199 | 3.7849 | 199 | 4.6076 | 209 | 6.1396 | 209 | 7.4665
[8 empty] | 180 | 0.51015 | 180 | 0.62928 | 182 | 0.72 | 182 | 0.88146 | 184 | 0.96069 | 184 | 1.1698 | 186 | 1.2183 | 186 | 1.4919 | 190 | 1.8315 | 190 | 2.2311 | 194 | 2.5473 | 194 | 3.0904 | 200 | 3.7501 | 200 | 4.5612 | 210 | 6.0858 | 210 | 7.3947
[8 empty] | 181 | 0.50504 | 181 | 0.62248 | 183 | 0.71285 | 183 | 0.87198 | 185 | 0.94195 | 185 | 1.1574 | 187 | 1.2065 | 187 | 1.4762 | 191 | 1.8141 | 191 | 2.2076 | 195 | 2.4995 | 195 | 3.0585 | 201 | 3.7157 | 201 | 4.5154 | 211 | 6.0328 | 211 | 7.3239
[8 empty] | 182 | 0.5 | 182 | 0.61579 | 184 | 0.70581 | 184 | 0.86266 | 186 | 0.93278 | 186 | 1.1451 | 188 | 1.1949 | 188 | 1.4606 | 192 | 1.7969 | 192 | 2.1845 | 196 | 2.4761 | 196 | 3.0271 | 202 | 3.6819 | 202 | 4.4704 | 212 | 5.9804 | 212 | 7.2542
[8 empty] | 183 | 0.49504 | 183 | 0.60921 | 185 | 0.69204 | 185 | 0.85349 | 187 | 0.92374 | 187 | 1.133 | 189 | 1.1834 | 189 | 1.4453 | 193 | 1.78 | 193 | 2.1618 | 197 | 2.4531 | 197 | 2.9961 | 203 | 3.6485 | 203 | 4.426 | 213 | 5.9287 | 213 | 7.1855
[8 empty] | 184 | 0.49015 | 184 | 0.60274 | 186 | 0.68531 | 186 | 0.84447 | 188 | 0.91484 | 188 | 1.1211 | 190 | 1.1721 | 190 | 1.4303 | 194 | 1.7633 | 194 | 2.1394 | 198 | 2.4303 | 198 | 2.9657 | 204 | 3.6156 | 204 | 4.3822 | 214 | 5.8777 | 214 | 7.1177
[8 empty] | 185 | 0.48058 | 185 | 0.59637 | 187 | 0.67867 | 187 | 0.83559 | 189 | 0.90607 | 189 | 1.1094 | 191 | 1.161 | 191 | 1.4155 | 195 | 1.7307 | 195 | 2.1173 | 199 | 2.4079 | 199 | 2.9357 | 205 | 3.551 | 205 | 4.3391 | 215 | 5.7776 | 215 | 7.0509
[8 empty] | 186 | 0.47591 | 186 | 0.5901 | 188 | 0.67213 | 188 | 0.82685 | 190 | 0.89742 | 190 | 1.0979 | 192 | 1.15 | 192 | 1.4009 | 196 | 1.7147 | 196 | 2.0956 | 200 | 2.3857 | 200 | 2.9061 | 206 | 3.5194 | 206 | 4.2966 | 216 | 5.7285 | 216 | 6.985
[8 empty] | 187 | 0.4713 | 187 | 0.58394 | 189 | 0.66568 | 189 | 0.81825 | 191 | 0.88889 | 191 | 1.0865 | 193 | 1.1392 | 193 | 1.3865 | 197 | 1.6989 | 197 | 2.0742 | 201 | 2.3639 | 201 | 2.877 | 207 | 3.4882 | 207 | 4.2548 | 217 | 5.68 | 217 | 6.92
[8 empty] | 188 | 0.46676 | 188 | 0.57787 | 190 | 0.65933 | 190 | 0.80978 | 192 | 0.88048 | 192 | 1.0754 | 194 | 1.1285 | 194 | 1.3724 | 198 | 1.6834 | 198 | 2.0532 | 202 | 2.3424 | 202 | 2.8483 | 208 | 3.4574 | 208 | 4.2136 | 218 | 5.6322 | 218 | 6.8559
[8 empty] | 189 | 0.46228 | 189 | 0.57189 | 191 | 0.65306 | 191 | 0.80145 | 193 | 0.8722 | 193 | 1.0644 | 195 | 1.1076 | 195 | 1.3585 | 199 | 1.668 | 199 | 2.0324 | 203 | 2.3211 | 203 | 2.8201 | 209 | 3.427 | 209 | 4.1729 | 219 | 5.5849 | 219 | 6.7927
[8 empty] | 190 | 0.45786 | 190 | 0.56602 | 192 | 0.64689 | 192 | 0.79325 | 194 | 0.86403 | 194 | 1.0536 | 196 | 1.0974 | 196 | 1.3448 | 200 | 1.6529 | 200 | 2.012 | 204 | 2.3002 | 204 | 2.7923 | 210 | 3.397 | 210 | 4.1329 | 220 | 5.5382 | 220 | 6.7304
[8 empty] | 191 | 0.45351 | 191 | 0.56023 | 193 | 0.6408 | 193 | 0.78518 | 195 | 0.84803 | 195 | 1.0429 | 197 | 1.0873 | 197 | 1.3313 | 201 | 1.638 | 201 | 1.9922 | 205 | 2.2591 | 205 | 2.7648 | 211 | 3.3674 | 211 | 4.0934 | 221 | 5.4921 | 221 | 6.6689
[8 empty] | 192 | 0.44923 | 192 | 0.55453 | 194 | 0.63479 | 194 | 0.77722 | 196 | 0.84019 | 196 | 1.0324 | 198 | 1.0774 | 198 | 1.318 | 202 | 1.6232 | 202 | 1.9726 | 206 | 2.239 | 206 | 2.7378 | 212 | 3.3381 | 212 | 4.0544 | 222 | 5.4466 | 222 | 6.6083
[8 empty] | 193 | 0.445 | 193 | 0.54893 | 195 | 0.62304 | 195 | 0.7694 | 197 | 0.83247 | 197 | 1.0221 | 199 | 1.0675 | 199 | 1.3049 | 203 | 1.6087 | 203 | 1.9533 | 207 | 2.2191 | 207 | 2.7112 | 213 | 3.3093 | 213 | 4.0161 | 223 | 5.4017 | 223 | 6.5485
[8 empty] | 194 | 0.44083 | 194 | 0.54341 | 196 | 0.61728 | 196 | 0.76169 | 198 | 0.82485 | 198 | 1.0119 | 200 | 1.0578 | 200 | 1.292 | 204 | 1.5944 | 204 | 1.9343 | 208 | 2.1995 | 208 | 2.685 | 214 | 3.2808 | 214 | 3.9782 | 224 | 5.3572 | 224 | 6.4895
[8 empty] | 195 | 0.43267 | 195 | 0.53797 | 197 | 0.61161 | 197 | 0.7541 | 199 | 0.81733 | 199 | 1.0019 | 201 | 1.0483 | 201 | 1.2793 | 205 | 1.5663 | 205 | 1.9156 | 209 | 2.1802 | 209 | 2.6591 | 215 | 3.2249 | 215 | 3.9409 | 225 | 5.27 | 225 | 6.4313
[8 empty] | 196 | 0.42867 | 196 | 0.53262 | 198 | 0.60601 | 198 | 0.74662 | 200 | 0.80992 | 200 | 0.992 | 202 | 1.0389 | 202 | 1.2668 | 206 | 1.5525 | 206 | 1.8972 | 210 | 2.1611 | 210 | 2.6336 | 216 | 3.1975 | 216 | 3.9042 | 226 | 5.2272 | 226 | 6.3738
[8 empty] | 197 | 0.42473 | 197 | 0.52734 | 199 | 0.60049 | 199 | 0.73925 | 201 | 0.8026 | 201 | 0.98227 | 203 | 1.0296 | 203 | 1.2545 | 207 | 1.5389 | 207 | 1.879 | 211 | 2.1423 | 211 | 2.6085 | 217 | 3.1705 | 217 | 3.8679 | 227 | 5.1849 | 227 | 6.3171
[8 empty] | 198 | 0.42084 | 198 | 0.52215 | 200 | 0.59504 | 200 | 0.732 | 202 | 0.79539 | 202 | 0.97269 | 204 | 1.0204 | 204 | 1.2423 | 208 | 1.5255 | 208 | 1.8611 | 212 | 2.1237 | 212 | 2.5837 | 218 | 3.1437 | 218 | 3.8321 | 228 | 5.1432 | 228 | 6.2612
[8 empty] | 199 | 0.41701 | 199 | 0.51704 | 201 | 0.58967 | 201 | 0.72485 | 203 | 0.78827 | 203 | 0.96325 | 205 | 1.0024 | 205 | 1.2303 | 209 | 1.5123 | 209 | 1.8435 | 213 | 2.1053 | 213 | 2.5593 | 219 | 3.1174 | 219 | 3.7969 | 229 | 5.1019 | 229 | 6.206
[8 empty] | 200 | 0.41322 | 200 | 0.512 | 202 | 0.58437 | 202 | 0.71781 | 204 | 0.78125 | 204 | 0.95395 | 206 | 0.99362 | 206 | 1.2185 | 210 | 1.4992 | 210 | 1.8261 | 214 | 2.0872 | 214 | 2.5353 | 220 | 3.0913 | 220 | 3.7621 | 230 | 5.0611 | 230 | 6.1516
[8 empty] | 201 | 0.40949 | 201 | 0.50704 | 203 | 0.57914 | 203 | 0.71088 | 205 | 0.76748 | 205 | 0.94478 | 207 | 0.98492 | 207 | 1.2069 | 211 | 1.4863 | 211 | 1.8089 | 215 | 2.0516 | 215 | 2.5115 | 221 | 3.0656 | 221 | 3.7277 | 231 | 5.0208 | 231 | 6.0978
[8 empty] | 202 | 0.40581 | 202 | 0.50215 | 204 | 0.57398 | 204 | 0.70404 | 206 | 0.76074 | 206 | 0.93574 | 208 | 0.97634 | 208 | 1.1954 | 212 | 1.4736 | 212 | 1.792 | 216 | 2.0342 | 216 | 2.4881 | 222 | 3.0402 | 222 | 3.6939 | 232 | 4.9809 | 232 | 6.0448
[8 empty] | 203 | 0.40218 | 203 | 0.49733 | 205 | 0.56387 | 205 | 0.69731 | 207 | 0.75408 | 207 | 0.92684 | 209 | 0.96786 | 209 | 1.1841 | 213 | 1.461 | 213 | 1.7753 | 217 | 2.017 | 217 | 2.4651 | 223 | 3.0151 | 223 | 3.6605 | 233 | 4.9416 | 233 | 5.9924
[8 empty] | 204 | 0.3986 | 204 | 0.49258 | 206 | 0.55891 | 206 | 0.69067 | 208 | 0.74751 | 208 | 0.91807 | 210 | 0.9595 | 210 | 1.173 | 214 | 1.4486 | 214 | 1.7589 | 218 | 2 | 218 | 2.4423 | 224 | 2.9903 | 224 | 3.6276 | 234 | 4.9027 | 234 | 5.9407
[8 empty] | 205 | 0.39157 | 205 | 0.48791 | 207 | 0.55402 | 207 | 0.68413 | 209 | 0.74102 | 209 | 0.90942 | 211 | 0.95125 | 211 | 1.162 | 215 | 1.4243 | 215 | 1.7427 | 219 | 1.9834 | 219 | 2.4199 | 225 | 2.9416 | 225 | 3.5951 | 235 | 4.8643 | 235 | 5.8897
[8 empty] | 206 | 0.38813 | 206 | 0.4833 | 208 | 0.54919 | 208 | 0.67768 | 210 | 0.73462 | 210 | 0.90089 | 212 | 0.9431 | 212 | 1.1512 | 216 | 1.4123 | 216 | 1.7267 | 220 | 1.9671 | 220 | 2.3977 | 226 | 2.9177 | 226 | 3.563 | 236 | 4.7887 | 236 | 5.8393
[8 empty] | 207 | 0.38473 | 207 | 0.47876 | 209 | 0.54442 | 209 | 0.67133 | 211 | 0.7283 | 211 | 0.89248 | 213 | 0.93506 | 213 | 1.1405 | 217 | 1.4005 | 217 | 1.7109 | 221 | 1.9509 | 221 | 2.3759 | 227 | 2.8941 | 227 | 3.5314 | 237 | 4.7516 | 237 | 5.7896
[8 empty] | 208 | 0.38138 | 208 | 0.47428 | 210 | 0.53972 | 210 | 0.66506 | 212 | 0.72206 | 212 | 0.8842 | 214 | 0.92712 | 214 | 1.13 | 218 | 1.3889 | 218 | 1.6954 | 222 | 1.935 | 222 | 2.3544 | 228 | 2.8708 | 228 | 3.5002 | 238 | 4.7149 | 238 | 5.7405
[8 empty] | 209 | 0.37807 | 209 | 0.46986 | 211 | 0.53508 | 211 | 0.65889 | 213 | 0.7159 | 213 | 0.87603 | 215 | 0.91153 | 215 | 1.1196 | 219 | 1.3774 | 219 | 1.68 | 223 | 1.9192 | 223 | 2.3331 | 229 | 2.8478 | 229 | 3.4694 | 239 | 4.6787 | 239 | 5.692
[8 empty] | 210 | 0.37481 | 210 | 0.46551 | 212 | 0.53049 | 212 | 0.6528 | 214 | 0.70982 | 214 | 0.86797 | 216 | 0.90389 | 216 | 1.1094 | 220 | 1.366 | 220 | 1.6649 | 224 | 1.9036 | 224 | 2.3122 | 230 | 2.825 | 230 | 3.439 | 240 | 4.6428 | 240 | 5.6442
[8 empty] | 211 | 0.37158 | 211 | 0.46123 | 213 | 0.52597 | 213 | 0.64679 | 215 | 0.69789 | 215 | 0.86003 | 217 | 0.89634 | 217 | 1.0993 | 221 | 1.3548 | 221 | 1.65 | 225 | 1.8731 | 225 | 2.2915 | 231 | 2.8025 | 231 | 3.409 | 241 | 4.6074 | 241 | 5.5969
[8 empty] | 212 | 0.3684 | 212 | 0.457 | 214 | 0.5215 | 214 | 0.64088 | 216 | 0.69204 | 216 | 0.85219 | 218 | 0.88889 | 218 | 1.0894 | 222 | 1.3437 | 222 | 1.6352 | 226 | 1.858 | 226 | 2.2711 | 232 | 2.7803 | 232 | 3.3794 | 242 | 4.5723 | 242 | 5.5502
[8 empty] | 213 | 0.36526 | 213 | 0.45283 | 215 | 0.51274 | 215 | 0.63504 | 217 | 0.68626 | 217 | 0.84447 | 219 | 0.88153 | 219 | 1.0795 | 223 | 1.3328 | 223 | 1.6207 | 227 | 1.8432 | 227 | 2.251 | 233 | 2.7583 | 233 | 3.3501 | 243 | 4.5377 | 243 | 5.5041
[8 empty] | 214 | 0.36215 | 214 | 0.44872 | 216 | 0.50844 | 216 | 0.62928 | 218 | 0.68056 | 218 | 0.83685 | 220 | 0.87426 | 220 | 1.0698 | 224 | 1.322 | 224 | 1.6064 | 228 | 1.8285 | 228 | 2.2311 | 234 | 2.7366 | 234 | 3.3213 | 244 | 4.5034 | 244 | 5.4586
[8 empty] | 215 | 0.35607 | 215 | 0.44467 | 217 | 0.50419 | 217 | 0.62361 | 219 | 0.67492 | 219 | 0.82933 | 221 | 0.86708 | 221 | 1.0603 | 225 | 1.3007 | 225 | 1.5922 | 229 | 1.8141 | 229 | 2.2115 | 235 | 2.7151 | 235 | 3.2928 | 245 | 4.4361 | 245 | 5.4136
[8 empty] | 216 | 0.35308 | 216 | 0.44067 | 218 | 0.5 | 218 | 0.61801 | 220 | 0.66935 | 220 | 0.82192 | 222 | 0.85998 | 222 | 1.0509 | 226 | 1.2903 | 226 | 1.5783 | 230 | 1.7997 | 230 | 2.1922 | 236 | 2.673 | 236 | 3.2647 | 246 | 4.403 | 246 | 5.3692
[8 empty] | 217 | 0.35013 | 217 | 0.43673 | 219 | 0.49586 | 219 | 0.61249 | 221 | 0.66386 | 221 | 0.8146 | 223 | 0.85298 | 223 | 1.0416 | 227 | 1.28 | 227 | 1.5645 | 231 | 1.7856 | 231 | 2.1731 | 237 | 2.6522 | 237 | 3.2369 | 247 | 4.3702 | 247 | 5.3254
[8 empty] | 218 | 0.34722 | 218 | 0.43284 | 220 | 0.49177 | 220 | 0.60704 | 222 | 0.65843 | 222 | 0.80739 | 224 | 0.84606 | 224 | 1.0324 | 228 | 1.2698 | 228 | 1.5509 | 232 | 1.7716 | 232 | 2.1543 | 238 | 2.6318 | 238 | 3.2095 | 248 | 4.3378 | 248 | 5.282
[8 empty] | 219 | 0.34435 | 219 | 0.42901 | 221 | 0.48773 | 221 | 0.60167 | 223 | 0.65306 | 223 | 0.80027 | 225 | 0.83247 | 225 | 1.0234 | 229 | 1.2598 | 229 | 1.5375 | 233 | 1.7578 | 233 | 2.1357 | 239 | 2.6115 | 239 | 3.1825 | 249 | 4.3058 | 249 | 5.2392
[8 empty] | 220 | 0.34151 | 220 | 0.42522 | 222 | 0.48374 | 222 | 0.59637 | 224 | 0.64776 | 224 | 0.79325 | 226 | 0.82579 | 226 | 1.0144 | 230 | 1.2498 | 230 | 1.5243 | 234 | 1.7442 | 234 | 2.1173 | 240 | 2.5915 | 240 | 3.1557 | 250 | 4.2741 | 250 | 5.1969
[8 empty] | 221 | 0.3387 | 221 | 0.42149 | 223 | 0.4798 | 223 | 0.59114 | 225 | 0.63736 | 225 | 0.78632 | 227 | 0.8192 | 227 | 1.0056 | 231 | 1.24 | 231 | 1.5112 | 235 | 1.7307 | 235 | 2.0992 | 241 | 2.5717 | 241 | 3.1294 | 251 | 4.2428 | 251 | 5.1551
[8 empty] | 222 | 0.33593 | 222 | 0.41781 | 224 | 0.47591 | 224 | 0.58598 | 226 | 0.63225 | 226 | 0.77948 | 228 | 0.81269 | 228 | 0.99692 | 232 | 1.2303 | 232 | 1.4983 | 236 | 1.7041 | 236 | 2.0813 | 242 | 2.5522 | 242 | 3.1033 | 252 | 4.2118 | 252 | 5.1139
[8 empty] | 223 | 0.33319 | 223 | 0.41418 | 225 | 0.46826 | 225 | 0.58089 | 227 | 0.6272 | 227 | 0.77274 | 229 | 0.80625 | 229 | 0.98834 | 233 | 1.2207 | 233 | 1.4856 | 237 | 1.6911 | 237 | 2.0636 | 243 | 2.5328 | 243 | 3.0776 | 253 | 4.1812 | 253 | 5.0731
[8 empty] | 224 | 0.33049 | 224 | 0.4106 | 226 | 0.46451 | 226 | 0.57587 | 228 | 0.62221 | 228 | 0.76608 | 230 | 0.79989 | 230 | 0.97986 | 234 | 1.2112 | 234 | 1.473 | 238 | 1.6782 | 238 | 2.0462 | 244 | 2.5137 | 244 | 3.0522 | 254 | 4.1509 | 254 | 5.0328
[8 empty] | 225 | 0.32518 | 225 | 0.40706 | 227 | 0.4608 | 227 | 0.57091 | 229 | 0.61728 | 229 | 0.75951 | 231 | 0.7936 | 231 | 0.9715 | 235 | 1.2019 | 235 | 1.4606 | 239 | 1.6655 | 239 | 2.029 | 245 | 2.4761 | 245 | 3.0271 | 255 | 4.1209 | 255 | 4.993
[8 empty] | 226 | 0.32258 | 226 | 0.40357 | 228 | 0.45714 | 228 | 0.56602 | 230 | 0.61241 | 230 | 0.75302 | 232 | 0.78739 | 232 | 0.96325 | 236 | 1.1834 | 236 | 1.4484 | 240 | 1.6529 | 240 | 2.012 | 246 | 2.4576 | 246 | 3.0023 | 256 | 4.0618 | 256 | 4.9536
[8 empty] | 227 | 0.015625 | 227 | 0.40013 | 229 | 0.45351 | 229 | 0.56119 | 231 | 0.6076 | 231 | 0.74662 | 233 | 0.78125 | 233 | 0.9551 | 237 | 1.1744 | 237 | 1.4363 | 241 | 1.6404 | 241 | 1.9954 | 247 | 2.4394 | 247 | 2.9778 | 257 | 4.0328 | 257 | 4.9147
[8 empty] | 228 | 0.015625 | 228 | 0.39673 | 230 | 0.44994 | 230 | 0.55642 | 232 | 0.60285 | 232 | 0.7403 | 234 | 0.77518 | 234 | 0.94706 | 238 | 1.1654 | 238 | 1.4243 | 242 | 1.6281 | 242 | 1.9791 | 248 | 2.4213 | 248 | 2.9536 | 258 | 4.0041 | 258 | 4.8763
[8 empty] | 229 | 0.015625 | 229 | 0.39338 | 231 | 0.4464 | 231 | 0.55172 | 233 | 0.59814 | 233 | 0.73406 | 235 | 0.76918 | 235 | 0.93912 | 239 | 1.1566 | 239 | 1.4125 | 243 | 1.616 | 243 | 1.9629 | 249 | 2.4034 | 249 | 2.9297 | 259 | 3.9756 | 259 | 4.8383
[8 empty] | 230 | 0.015625 | 230 | 0.39007 | 232 | 0.44291 | 232 | 0.54708 | 234 | 0.5935 | 234 | 0.7279 | 236 | 0.7574 | 236 | 0.93128 | 240 | 1.1478 | 240 | 1.4009 | 244 | 1.6039 | 244 | 1.947 | 250 | 2.3857 | 250 | 2.9061 | 260 | 3.9475 | 260 | 4.8007
[8 empty] | 231 | 0.015625 | 231 | 0.38681 | 233 | 0.43945 | 233 | 0.54249 | 235 | 0.58891 | 235 | 0.72182 | 237 | 0.7516 | 237 | 0.92353 | 241 | 1.1392 | 241 | 1.3894 | 245 | 1.5802 | 245 | 1.9312 | 251 | 2.3682 | 251 | 2.8828 | 261 | 3.9197 | 261 | 4.7636
[8 empty] | 232 | 0.015625 | 232 | 0.38358 | 234 | 0.43604 | 234 | 0.53797 | 236 | 0.57988 | 236 | 0.71582 | 238 | 0.74588 | 238 | 0.91589 | 242 | 1.1306 | 242 | 1.378 | 246 | 1.5686 | 246 | 1.9156 | 252 | 2.3509 | 252 | 2.8598 | 262 | 3.8922 | 262 | 4.7269
[8 empty] | 233 | 0.015625 | 233 | 0.3804 | 235 | 0.43267 | 235 | 0.5335 | 237 | 0.57545 | 237 | 0.70989 | 239 | 0.74022 | 239 | 0.90834 | 243 | 1.1222 | 243 | 1.3668 | 247 | 1.5571 | 247 | 1.9002 | 253 | 2.3338 | 253 | 2.837 | 263 | 3.8649 | 263 | 4.6907
[8 empty] | 234 | 0.015625 | 234 | 0.37726 | 236 | 0.42604 | 236 | 0.52909 | 238 | 0.57106 | 238 | 0.70404 | 240 | 0.73462 | 240 | 0.90089 | 244 | 1.1138 | 244 | 1.3557 | 248 | 1.5457 | 248 | 1.885 | 254 | 2.3169 | 254 | 2.8145 | 264 | 3.838 | 264 | 4.6548
[8 empty] | 235 | 0.015625 | 235 | 0.37415 | 237 | 0.42278 | 237 | 0.52474 | 239 | 0.56673 | 239 | 0.69826 | 241 | 0.72909 | 241 | 0.89353 | 245 | 1.0974 | 245 | 1.3448 | 249 | 1.5345 | 249 | 1.87 | 255 | 2.3002 | 255 | 2.7923 | 265 | 3.7849 | 265 | 4.6194
[8 empty] | 236 | 0.015625 | 236 | 0.37109 | 238 | 0.41956 | 238 | 0.52044 | 240 | 0.56244 | 240 | 0.69256 | 242 | 0.72361 | 242 | 0.88626 | 246 | 1.0893 | 246 | 1.334 | 250 | 1.5233 | 250 | 1.8552 | 256 | 2.2672 | 256 | 2.7703 | 266 | 3.7587 | 266 | 4.5843
[8 empty] | 237 | 0.015625 | 237 | 0.36807 | 239 | 0.41637 | 239 | 0.51619 | 241 | 0.55821 | 241 | 0.68692 | 243 | 0.7182 | 243 | 0.87908 | 247 | 1.0813 | 247 | 1.3233 | 251 | 1.5123 | 251 | 1.8405 | 257 | 2.251 | 257 | 2.7486 | 267 | 3.7329 | 267 | 4.5497
[8 empty] | 238 | 0.015625 | 238 | 0.36508 | 240 | 0.41322 | 240 | 0.512 | 242 | 0.55402 | 242 | 0.68135 | 244 | 0.71285 | 244 | 0.87198 | 248 | 1.0734 | 248 | 1.3127 | 252 | 1.5014 | 252 | 1.8261 | 258 | 2.235 | 258 | 2.7271 | 268 | 3.7073 | 268 | 4.5154
[8 empty] | 239 | 0.015625 | 239 | 0.36213 | 241 | 0.41011 | 241 | 0.50786 | 243 | 0.54987 | 243 | 0.67586 | 245 | 0.70233 | 245 | 0.86498 | 249 | 1.0656 | 249 | 1.3023 | 253 | 1.4906 | 253 | 1.8117 | 259 | 2.2191 | 259 | 2.7059 | 269 | 3.6819 | 269 | 4.4816
[8 empty] | 240 | 0.015625 | 240 | 0.35922 | 242 | 0.40703 | 242 | 0.50377 | 244 | 0.54578 | 244 | 0.67043 | 246 | 0.69716 | 246 | 0.85806 | 250 | 1.0578 | 250 | 1.292 | 254 | 1.4799 | 254 | 1.7976 | 260 | 2.2034 | 260 | 2.685 | 270 | 3.6568 | 270 | 4.4481
[8 empty] | 241 | 0.015625 | 241 | 0.35635 | 243 | 0.40399 | 243 | 0.49973 | 245 | 0.53772 | 245 | 0.66506 | 247 | 0.69204 | 247 | 0.85122 | 251 | 1.0502 | 251 | 1.2818 | 255 | 1.4694 | 255 | 1.7836 | 261 | 2.1879 | 261 | 2.6642 | 271 | 3.632 | 271 | 4.415
[8 empty] | 242 | 0.015625 | 242 | 0.35351 | 244 | 0.40098 | 244 | 0.49574 | 246 | 0.53376 | 246 | 0.65976 | 248 | 0.68698 | 248 | 0.84447 | 252 | 1.0426 | 252 | 1.2718 | 256 | 1.4486 | 256 | 1.7698 | 262 | 2.1725 | 262 | 2.6438 | 272 | 3.6074 | 272 | 4.3822
[8 empty] | 243 | 0.015625 | 243 | 0.3507 | 245 | 0.39506 | 245 | 0.4918 | 247 | 0.52984 | 247 | 0.65453 | 249 | 0.68198 | 249 | 0.83779 | 253 | 1.0351 | 253 | 1.2618 | 257 | 1.4384 | 257 | 1.7562 | 263 | 2.1573 | 263 | 2.6235 | 273 | 0.015625 | 273 | 4.3498
[8 empty] | 244 | 0.015625 | 244 | 0.34793 | 246 | 0.39215 | 246 | 0.48791 | 248 | 0.52597 | 248 | 0.64936 | 250 | 0.67702 | 250 | 0.8312 | 254 | 1.0277 | 254 | 1.252 | 258 | 1.4283 | 258 | 1.7427 | 264 | 2.1423 | 264 | 2.6035 | 274 | 0.015625 | 274 | 4.3178
[8 empty] | 245 | 0.015625 | 245 | 0.34519 | 247 | 0.38927 | 247 | 0.48406 | 249 | 0.52214 | 249 | 0.64425 | 251 | 0.67213 | 251 | 0.82469 | 255 | 1.0204 | 255 | 1.2423 | 259 | 1.4183 | 259 | 1.7293 | 265 | 2.1126 | 265 | 2.5837 | 275 | 0.015625 | 275 | 4.2861
[8 empty] | 246 | 0.015625 | 246 | 0.34249 | 248 | 0.38643 | 248 | 0.48026 | 250 | 0.51835 | 250 | 0.6392 | 252 | 0.66728 | 252 | 0.81825 | 256 | 1.006 | 256 | 1.2327 | 260 | 1.4084 | 260 | 1.7161 | 266 | 2.098 | 266 | 2.5642 | 276 | 0.015625 | 276 | 4.2548
[8 empty] | 247 | 0.015625 | 247 | 0.33982 | 249 | 0.38361 | 249 | 0.47651 | 251 | 0.5146 | 251 | 0.63421 | 253 | 0.66249 | 253 | 0.81189 | 257 | 0.99889 | 257 | 1.2232 | 261 | 1.3986 | 261 | 1.7031 | 267 | 2.0836 | 267 | 2.5448 | 277 | 0.015625 | 277 | 4.2238
[8 empty] | 248 | 0.015625 | 248 | 0.33718 | 250 | 0.38083 | 250 | 0.4728 | 252 | 0.51089 | 252 | 0.62928 | 254 | 0.65775 | 254 | 0.8056 | 258 | 0.99187 | 258 | 1.2139 | 262 | 1.3889 | 262 | 1.6902 | 268 | 2.0693 | 268 | 2.5257 | 278 | 0.015625 | 278 | 4.1932
[8 empty] | 249 | 0.015625 | 249 | 0.33458 | 251 | 0.37807 | 251 | 0.46914 | 253 | 0.50722 | 253 | 0.62441 | 255 | 0.65306 | 255 | 0.79939 | 259 | 0.98492 | 259 | 1.2046 | 263 | 1.3793 | 263 | 1.6775 | 269 | 2.0552 | 269 | 2.5068 | 279 | 0.015625 | 279 | 4.1628
[8 empty] | 250 | 0.015625 | 250 | 0.03334 | 252 | 0.37535 | 252 | 0.46551 | 254 | 0.50359 | 254 | 0.6196 | 256 | 0.64383 | 256 | 0.79325 | 260 | 0.97804 | 260 | 1.1954 | 264 | 1.3698 | 264 | 1.6649 | 270 | 2.0412 | 270 | 2.4881 | 280 | 0.015625 | 280 | 4.1329
[8 empty] | 453 | 0.015625 | 453 | 0.03334 | 253 | 0.37265 | 253 | 0.46194 | 255 | 0.5 | 255 | 0.61485 | 257 | 0.63929 | 257 | 0.78718 | 261 | 0.97124 | 261 | 1.1864 | 265 | 1.3511 | 265 | 1.6524 | 271 | 2.0273 | 271 | 2.4696 | 281 | 0.015625 | 281 | 4.1032
[8 empty] | 454 | 0.011042 | 454 | 0.03334 | 254 | 0.36998 | 254 | 0.4584 | 256 | 0.49293 | 256 | 0.61014 | 258 | 0.63479 | 258 | 0.78118 | 262 | 0.96451 | 262 | 1.1774 | 266 | 1.3419 | 266 | 1.6401 | 272 | 2.0136 | 272 | 2.4514 | 282 | 0.015625 | 282 | 4.0738
[8 empty] | 455 | 0.001 | 455 | 0.03334 | 255 | 0.36735 | 255 | 0.45491 | 257 | 0.48946 | 257 | 0.6055 | 259 | 0.63035 | 259 | 0.77526 | 263 | 0.95784 | 263 | 1.1686 | 267 | 1.3328 | 267 | 1.628 | 273 | 0.015625 | 273 | 2.4333 | 283 | 0.015625 | 283 | 4.0448
[8 empty] | 500 | 0.001 | 500 | 0.03334 | 256 | 0.36215 | 256 | 0.45145 | 258 | 0.48601 | 258 | 0.60091 | 260 | 0.62595 | 260 | 0.7694 | 264 | 0.95125 | 264 | 1.1598 | 268 | 1.3238 | 268 | 1.6159 | 274 | 0.015625 | 274 | 2.4154 | 284 | 0.015625 | 284 | 4.0161
[8 empty] | 501 | 0.001 | 501 | 0.01667 | 257 | 0.3596 | 257 | 0.44804 | 259 | 0.48261 | 259 | 0.59637 | 261 | 0.62159 | 261 | 0.7636 | 265 | 0.93826 | 265 | 1.1512 | 269 | 1.3148 | 269 | 1.604 | 275 | 0.015625 | 275 | 2.3977 | 285 | 0.015625 | 285 | 3.9876
[8 empty] | 6300 | 0.001 | 6300 | 0.01667 | 258 | 0.35707 | 258 | 0.44467 | 260 | 0.47924 | 260 | 0.59188 | 262 | 0.61728 | 262 | 0.75788 | 266 | 0.93187 | 266 | 1.1426 | 270 | 1.306 | 270 | 1.5922 | 276 | 0.015625 | 276 | 2.3802 | 286 | 0.015625 | 286 | 3.9595
[12 empty] | 259 | 0.35457 | 259 | 0.44133 | 261 | 0.47591 | 261 | 0.58745 | 263 | 0.61302 | 263 | 0.75222 | 267 | 0.92554 | 267 | 1.1342 | 271 | 1.2972 | 271 | 1.5806 | 277 | 0.015625 | 277 | 2.3629 | 287 | 0.015625 | 287 | 3.9317
[12 empty] | 260 | 0.3521 | 260 | 0.43804 | 262 | 0.47261 | 262 | 0.58306 | 264 | 0.6088 | 264 | 0.74662 | 268 | 0.91928 | 268 | 1.1258 | 272 | 1.2886 | 272 | 1.5691 | 278 | 0.015625 | 278 | 2.3458 | 288 | 0.015625 | 288 | 3.9042
[12 empty] | 261 | 0.34965 | 261 | 0.43478 | 263 | 0.46934 | 263 | 0.57873 | 265 | 0.60049 | 265 | 0.74109 | 269 | 0.91308 | 269 | 1.1176 | 273 | 0.015625 | 273 | 1.5577 | 279 | 0.015625 | 279 | 2.3289 | 289 | 0.015625 | 289 | 3.8769
[12 empty] | 262 | 0.34722 | 262 | 0.43156 | 264 | 0.46611 | 264 | 0.57444 | 266 | 0.5964 | 266 | 0.73561 | 270 | 0.90694 | 270 | 1.1094 | 274 | 0.015625 | 274 | 1.5465 | 280 | 0.015625 | 280 | 2.3122 | 290 | 0.015625 | 290 | 3.85
[12 empty] | 263 | 0.34482 | 263 | 0.42837 | 265 | 0.45975 | 265 | 0.57021 | 267 | 0.59235 | 267 | 0.7302 | 271 | 0.90086 | 271 | 1.1013 | 275 | 0.015625 | 275 | 1.5353 | 281 | 0.015625 | 281 | 2.2956 | 291 | 0.015625 | 291 | 3.8233
[12 empty] | 264 | 0.34245 | 264 | 0.42522 | 266 | 0.45662 | 266 | 0.56602 | 268 | 0.58834 | 268 | 0.72485 | 272 | 0.89484 | 272 | 1.0933 | 276 | 0.015625 | 276 | 1.5243 | 282 | 0.015625 | 282 | 2.2792 | 292 | 0.015625 | 292 | 3.7969
[12 empty] | 265 | 0.33777 | 265 | 0.42211 | 267 | 0.45351 | 267 | 0.56187 | 269 | 0.58437 | 269 | 0.71956 | 273 | 0.015625 | 273 | 1.0854 | 277 | 0.015625 | 277 | 1.5134 | 283 | 0.015625 | 283 | 2.263 | 293 | 0.015625 | 293 | 3.7707
[12 empty] | 266 | 0.33547 | 266 | 0.41903 | 268 | 0.45045 | 268 | 0.55778 | 270 | 0.58044 | 270 | 0.71433 | 274 | 0.015625 | 274 | 1.0776 | 278 | 0.015625 | 278 | 1.5026 | 284 | 0.015625 | 284 | 2.247 | 294 | 0.015625 | 294 | 3.7449
[12 empty] | 267 | 0.33319 | 267 | 0.41599 | 269 | 0.44741 | 269 | 0.55373 | 271 | 0.57655 | 271 | 0.70916 | 275 | 0.015625 | 275 | 1.0698 | 279 | 0.015625 | 279 | 1.4919 | 285 | 0.015625 | 285 | 2.2311 | 295 | 0.015625 | 295 | 3.7193
[12 empty] | 268 | 0.33094 | 268 | 0.41298 | 270 | 0.4444 | 270 | 0.54972 | 272 | 0.5727 | 272 | 0.70404 | 276 | 0.015625 | 276 | 1.0622 | 280 | 0.015625 | 280 | 1.4814 | 286 | 0.015625 | 286 | 2.2154 | 296 | 0.015625 | 296 | 3.6939
[12 empty] | 269 | 0.32871 | 269 | 0.41 | 271 | 0.44142 | 271 | 0.54576 | 273 | 0.015625 | 273 | 0.69898 | 277 | 0.015625 | 277 | 1.0546 | 281 | 0.015625 | 281 | 1.4709 | 287 | 0.015625 | 287 | 2.1999 | 297 | 0.015625 | 297 | 3.6688
[12 empty] | 270 | 0.3265 | 270 | 0.40706 | 272 | 0.43847 | 272 | 0.54184 | 274 | 0.015625 | 274 | 0.69398 | 278 | 0.015625 | 278 | 1.0471 | 282 | 0.015625 | 282 | 1.4606 | 288 | 0.015625 | 288 | 2.1845 | 298 | 0.015625 | 298 | 3.644
[12 empty] | 271 | 0.32431 | 271 | 0.40415 | 273 | 0.015625 | 273 | 0.53797 | 275 | 0.015625 | 275 | 0.68902 | 279 | 0.015625 | 279 | 1.0397 | 283 | 0.015625 | 283 | 1.4504 | 289 | 0.015625 | 289 | 2.1693 | 299 | 0.015625 | 299 | 3.6194
[12 empty] | 272 | 0.32214 | 272 | 0.40127 | 274 | 0.015625 | 274 | 0.53414 | 276 | 0.015625 | 276 | 0.68413 | 280 | 0.015625 | 280 | 1.0324 | 284 | 0.015625 | 284 | 1.4403 | 290 | 0.015625 | 290 | 2.1543 | 300 | 0.015625 | 300 | 0.03334
[12 empty] | 273 | 0.015625 | 273 | 0.39843 | 275 | 0.015625 | 275 | 0.53035 | 277 | 0.015625 | 277 | 0.67928 | 281 | 0.015625 | 281 | 1.0252 | 285 | 0.015625 | 285 | 1.4303 | 291 | 0.015625 | 291 | 2.1394 | 453 | 0.015625 | 453 | 0.03334
[12 empty] | 274 | 0.015625 | 274 | 0.39561 | 276 | 0.015625 | 276 | 0.5266 | 278 | 0.015625 | 278 | 0.67449 | 282 | 0.015625 | 282 | 1.018 | 286 | 0.015625 | 286 | 1.4204 | 292 | 0.015625 | 292 | 2.1246 | 454 | 0.011042 | 454 | 0.03334
[12 empty] | 275 | 0.015625 | 275 | 0.39283 | 277 | 0.015625 | 277 | 0.52289 | 279 | 0.015625 | 279 | 0.66975 | 283 | 0.015625 | 283 | 1.0109 | 287 | 0.015625 | 287 | 1.4106 | 293 | 0.015625 | 293 | 2.11 | 455 | 0.001 | 455 | 0.03334
[12 empty] | 276 | 0.015625 | 276 | 0.39007 | 278 | 0.015625 | 278 | 0.51922 | 280 | 0.015625 | 280 | 0.66506 | 284 | 0.015625 | 284 | 1.0039 | 288 | 0.015625 | 288 | 1.4009 | 294 | 0.015625 | 294 | 2.0956 | 500 | 0.001 | 500 | 0.03334
[12 empty] | 277 | 0.015625 | 277 | 0.38735 | 279 | 0.015625 | 279 | 0.51559 | 281 | 0.015625 | 281 | 0.66042 | 285 | 0.015625 | 285 | 0.99692 | 289 | 0.015625 | 289 | 1.3913 | 295 | 0.015625 | 295 | 2.0813 | 501 | 0.001 | 501 | 0.01667
[12 empty] | 278 | 0.015625 | 278 | 0.38465 | 280 | 0.015625 | 280 | 0.512 | 282 | 0.015625 | 282 | 0.65583 | 286 | 0.015625 | 286 | 0.99004 | 290 | 0.015625 | 290 | 1.3818 | 296 | 0.015625 | 296 | 2.0672 | 6300 | 0.001 | 6300 | 0.01667
[12 empty] | 279 | 0.015625 | 279 | 0.38198 | 281 | 0.015625 | 281 | 0.50845 | 283 | 0.015625 | 283 | 0.65129 | 287 | 0.015625 | 287 | 0.98324 | 291 | 0.015625 | 291 | 1.3724 | 297 | 0.015625 | 297 | 2.0532
[12 empty] | 280 | 0.015625 | 280 | 0.37935 | 282 | 0.015625 | 282 | 0.50493 | 284 | 0.015625 | 284 | 0.64679 | 288 | 0.015625 | 288 | 0.97651 | 292 | 0.015625 | 292 | 1.3631 | 298 | 0.015625 | 298 | 2.0393
[12 empty] | 281 | 0.015625 | 281 | 0.37674 | 283 | 0.015625 | 283 | 0.50146 | 285 | 0.015625 | 285 | 0.64235 | 289 | 0.015625 | 289 | 0.96984 | 293 | 0.015625 | 293 | 1.3539 | 299 | 0.015625 | 299 | 2.0256
[12 empty] | 282 | 0.015625 | 282 | 0.37415 | 284 | 0.015625 | 284 | 0.49801 | 286 | 0.015625 | 286 | 0.63795 | 290 | 0.015625 | 290 | 0.96325 | 294 | 0.015625 | 294 | 1.3448 | 300 | 0.015625 | 300 | 0.03334
[12 empty] | 283 | 0.015625 | 283 | 0.3716 | 285 | 0.015625 | 285 | 0.49461 | 287 | 0.015625 | 287 | 0.63359 | 291 | 0.015625 | 291 | 0.95672 | 295 | 0.015625 | 295 | 1.3358 | 453 | 0.015625 | 453 | 0.03334
[12 empty] | 284 | 0.015625 | 284 | 0.36907 | 286 | 0.015625 | 286 | 0.49124 | 288 | 0.015625 | 288 | 0.62928 | 292 | 0.015625 | 292 | 0.95026 | 296 | 0.015625 | 296 | 1.3268 | 454 | 0.011042 | 454 | 0.03334
[12 empty] | 285 | 0.015625 | 285 | 0.36657 | 287 | 0.015625 | 287 | 0.48791 | 289 | 0.015625 | 289 | 0.62502 | 293 | 0.015625 | 293 | 0.94387 | 297 | 0.015625 | 297 | 1.318 | 455 | 0.001 | 455 | 0.03334
[12 empty] | 286 | 0.015625 | 286 | 0.3641 | 288 | 0.015625 | 288 | 0.48461 | 290 | 0.015625 | 290 | 0.6208 | 294 | 0.015625 | 294 | 0.93754 | 298 | 0.015625 | 298 | 1.3092 | 500 | 0.001 | 500 | 0.03334
[12 empty] | 287 | 0.015625 | 287 | 0.36165 | 289 | 0.015625 | 289 | 0.48134 | 291 | 0.015625 | 291 | 0.61662 | 295 | 0.015625 | 295 | 0.93128 | 299 | 0.015625 | 299 | 1.3006 | 501 | 0.001 | 501 | 0.01667
[12 empty] | 288 | 0.015625 | 288 | 0.35922 | 290 | 0.015625 | 290 | 0.47811 | 292 | 0.015625 | 292 | 0.61249 | 296 | 0.015625 | 296 | 0.92508 | 300 | 0.015625 | 300 | 0.03334 | 6300 | 0.001 | 6300 | 0.01667
[12 empty] | 289 | 0.015625 | 289 | 0.35682 | 291 | 0.015625 | 291 | 0.47491 | 293 | 0.015625 | 293 | 0.6084 | 297 | 0.015625 | 297 | 0.91894 | 453 | 0.015625 | 453 | 0.03334
[12 empty] | 290 | 0.015625 | 290 | 0.35445 | 292 | 0.015625 | 292 | 0.47175 | 294 | 0.015625 | 294 | 0.60435 | 298 | 0.015625 | 298 | 0.91286 | 454 | 0.011042 | 454 | 0.03334
[12 empty] | 291 | 0.015625 | 291 | 0.3521 | 293 | 0.015625 | 293 | 0.46862 | 295 | 0.015625 | 295 | 0.60034 | 299 | 0.015625 | 299 | 0.90684 | 455 | 0.001 | 455 | 0.03334
[12 empty] | 292 | 0.015625 | 292 | 0.34977 | 294 | 0.015625 | 294 | 0.46551 | 296 | 0.015625 | 296 | 0.59637 | 300 | 0.015625 | 300 | 0.03334 | 500 | 0.001 | 500 | 0.03334
[12 empty] | 293 | 0.015625 | 293 | 0.34747 | 295 | 0.015625 | 295 | 0.46245 | 297 | 0.015625 | 297 | 0.59244 | 453 | 0.015625 | 453 | 0.03334 | 501 | 0.001 | 501 | 0.01667
[12 empty] | 294 | 0.015625 | 294 | 0.34519 | 296 | 0.015625 | 296 | 0.45941 | 298 | 0.015625 | 298 | 0.58855 | 454 | 0.011042 | 454 | 0.03334 | 6300 | 0.001 | 6300 | 0.01667
[12 empty] | 295 | 0.015625 | 295 | 0.34294 | 297 | 0.015625 | 297 | 0.4564 | 299 | 0.015625 | 299 | 0.5847 | 455 | 0.001 | 455 | 0.03334
[12 empty] | 296 | 0.015625 | 296 | 0.34071 | 298 | 0.015625 | 298 | 0.45342 | 300 | 0.015625 | 300 | 0.03334 | 500 | 0.001 | 500 | 0.03334
[12 empty] | 297 | 0.015625 | 297 | 0.3385 | 299 | 0.015625 | 299 | 0.45047 | 453 | 0.015625 | 453 | 0.03334 | 501 | 0.001 | 501 | 0.01667
[12 empty] | 298 | 0.015625 | 298 | 0.33631 | 300 | 0.015625 | 300 | 0.03334 | 454 | 0.011042 | 454 | 0.03334 | 6300 | 0.001 | 6300 | 0.01667
[12 empty] | 299 | 0.015625 | 299 | 0.33414 | 453 | 0.015625 | 453 | 0.03334 | 455 | 0.001 | 455 | 0.03334
[12 empty] | 300 | 0.015625 | 300 | 0.03334 | 454 | 0.011042 | 454 | 0.03334 | 500 | 0.001 | 500 | 0.03334
[12 empty] | 453 | 0.015625 | 453 | 0.03334 | 455 | 0.001 | 455 | 0.03334 | 501 | 0.001 | 501 | 0.01667
[12 empty] | 454 | 0.011042 | 454 | 0.03334 | 500 | 0.001 | 500 | 0.03334 | 6300 | 0.001 | 6300 | 0.01667
[12 empty] | 455 | 0.001 | 455 | 0.03334 | 501 | 0.001 | 501 | 0.01667
[12 empty] | 500 | 0.001 | 500 | 0.03334 | 6300 | 0.001 | 6300 | 0.01667
[12 empty] | 501 | 0.001 | 501 | 0.01667
[12 empty] | 6300 | 0.001 | 6300 | 0.01667